## Slide 1: Multi-Period Optimal Power Flow (MP-OPF) for Power Distribution Systems with Renewables and Battery Storage
Team WSU
Aryan Ritwajeet Jha, Graduate Research Assistant1
Dr. Subho Paul, Postdoctoral Research Associate1
Dr. Anamika Dubey, Associate Professor1
1 Energy Systems Innovation Center, School of Electrical Engineering and Computer Science, Voiland College of Engineering, Washington State University, Pullman
Notes: Remember to hit the reset button to make sure all the page elements react properly.
There are 20 different layouts that you can choose from.

## Slide 2: Overall Scope of the problem System Description and Objective
A radial distribution grid with multiple Grid Edge Resources.
Several EDO Nodes, which aggregate a portion of the Grid Edge Resources, and communicate and control them as per communication received from OpenDSO controllers.
OpenDSO controllers receive state variables from the grid, including those from EDO nodes, and load and DER generation forecast for the entire horizon.
OpenDSO controllers need to communicate amongst themselves (details in the algorithm).
The goal: To minimize some objective function , say line-losses or cost of substation power for the whole horizon of time-period .
Controllable variables (example):

## Slide 3: Overall Scope of the problem Algorithm and Communication Architecture
OpenDSO-System Operator (Forecast)
OpenDSO-Measurement Devices
OpenDSO-EDO
OpenDSO-OpenDSO

## Slide 4: Nature of Aggregated Edo Nodes
Grid Edge Resources over multiple buildings aggregated to form Edo Nodes.
We model them as Batteries, which introduces temporal coupling between OPF solutions at individual time-steps.
This mandates MPOPF
Our model is based on the Generalized Battery Model as given in [2].
Exception 1: Lifetime dissipation is not modelled.
Exception 2: Currently limits such as charging/discharging limits are assumed to be constant over time (in one day).

## Slide 5: Network being tested on
Current problem statement
  Test Case: IEEE123 Node System with Distributed Energy Resources (DERs) and Batteries.
  Balanced three-phase (with no phase coupling, akin to single-phase) power distribution network.
  Objective: Solve for Optimal Power Flow (OPF) for a horizon time interval of for a given objective function, say loss minimization.

## Slide 6: Network being tested on
ENApp Approach [1]
  Divide the network into several areas to solve for their Optimal Power Flow solutions separately, with exchange of boundary variables after every ‘macro-iteration’.
A previous model of the test system. Currently the system has DERs and Batteries on of the nodes with non-zero loads.

## Slide 7
A simpler schematic for D-OPF.

## Slide 8
A simpler schematic for MP-D-OPF for three time-steps
(

## Slide 9
What is currently being done? MP-DOPF in Brute Force

## Slide 10
What is will be done? A ‘true’ MP-DOPF using Differential Dynamic Programming (Currently under formulation, variables not explained here) [3]

## Slide 11: Overall Scope of the problem Algorithm and Communication Architecture
OpenDSO-System Operator (Forecast)
OpenDSO-Measurement Devices
OpenDSO-EDO
OpenDSO-OpenDSO

## Slide 12: Goal of Avista (problem objective for System Operator)
Problem objective of System Operator: Currently Modelled Use Case: Loss minimization
Use case communicated to all OpenDSO controllers
All OpenDSO controllers procure the models for the respective EDO nodes (the grid edge models: currently we’re modelling these as batteries, but generalized battery model can also be used, but we can make any other model work too which captures flexibility over time.)
Upon getting that, they locally optimize for their area
Then share the boundary information with the neighbouring OpenDSO nodes
Previous two steps are repeated until boundary values are converged.

## Slide 13: Problem Statement
  Given the State of Charges of all batteries in a grid at the beginning of a horizon interval ( representing the set of nodes with Batteries, along with predictions for other non-controllable parameter values like :
  Solve for Optimal Power Flow of the system, with the objective of minimizing line losses across the entire horizon of time interval

## Slide 14: Problem Statement
  Given the State of Charges of all batteries in a grid at the beginning of a horizon interval ( representing the set of nodes with Batteries, along with other non-controllable parameter values like :
  Solve for Optimal Power Flow of the system, with the objective of minimizing line losses across the entire horizon of time interval
  while making sure that:
  1. (the SOC of the battery at every point of the simulation) stays in permissible limits
  2. The OPF Solution is physically consistent. For no node containing a battery, is . In other words, make sure that Complementarity of Discharging and Charging is ensured. Alternatively, Simultaneous Charging and Discharging (SCD) is avoided.
  3. Other usual OPF physical constraints are also satisfied.
  4. Terminal SOC is same as initial.

## Slide 15: Simulation Parameters
Objective: Minimize Line Losses for whole horizon
System: IEEE Node System
Phase: Balanced (no phase coupling)
Supply: DERs (PVs): Forecasted, varying with . Batteries at select (about of total) nodes. Substation.
Demand: Forecasted. Varying with
Control: Inverter Reactive Power Control for DERs and Batteries. Battery Charging/Discharging.
Number of discrete time-steps: (can be changed)
Duration per time-step: min.

## Slide 16: Simulation Process of the current, brute-force algorithm
Start
--------------------------------------------
Known:
---------------------------------------------
while “(Spatial) boundary variables are NOT equal in value for all connected parent-child areas”
  Run OPF for minimizing the losses across the horizon for each area, in parallel. This is called as a macro-iteration.
  Exchange (spatial) boundary variables between all sets of connected parent-child areas.
end
-----------------------------------------------
Stop

## Slide 17: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: BFM Constraints with Battery and DER decision variables.
Line Losses
Real Powerflow from a bus into the network
Reactive Powerflow from a bus into the network
Kirchhoff's Voltage Law (KVL)
Current Magnitude in a branch

## Slide 18: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: BFM Constraints with Battery and DER decision variables.
Line Losses
DER Inverter Reactive Power
Nodal Voltage Limits

## Slide 19: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: BFM Constraints with Battery and DER decision variables.
Line Losses
Battery State of Charge Equation (this equation is temporally coupled, or has ‘memory’)

## Slide 20: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: BFM Constraints with Battery and DER decision variables.
Line Losses
Battery SOC Permissible Limits
Battery Inverter Reactive Power Limits
Battery Charging and Discharging Power Limits

## Slide 21: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: Tweaking the Objective Function to satisfy some more constraints.
Line Losses
Ensures Complementarity of Charging and Discharging, or alternatively, ensure there’s no SCD.
For minimizing the deviation between end-of-day battery SOC and a reference SOC.

## Slide 22: Optimization Formulation
(Integer-Constraint Relaxed) The Full Non-linear Optimization Problem
Real Powerflow from a bus into the network
Reactive Powerflow from a bus into the network
Kirchhoff's Voltage Law (KVL)
Current Magnitude in a branch
#Types of variables
#Variables
#Equality Constraints
(Non-Linear)
DER Generation (forecasted, non-controllable)
Loads (forecasted, non-controllable)
Line Losses
Ensures Complementarity of Charging and Discharging, or alternatively, ensure there’s no SCD.
For minimizing the deviation between end-of-day battery SOC and a reference SOC.
Battery State of Charge Equation (temporally coupled) with complementarity relaxed.

## Slide 23: Conclusion and Discussion
Major Observations:
Batteries were modelled correctly, i.e. no Simultaneous Charging and Discharging was observed.
Terminal SOC values (SOC values at end of day) mostly kept close to the original SOC values (beginning of day).
Questions: Currently the EDO Nodes have been modelled as batteries, but different models can be accommodated. What kind of models are Avista expecting?
What kind of objective function is Avista looking to optimize? Currently for line losses, the EDO nodes are operated under direct control, but for price signal inclusion, indirect control can be imposed on the EDO nodes (price signal data will be needed).

## Slide 24: Current Status of Simulation and Results
What has been done
A variety of simulation runs have been modelled and run for the sake of benchmarking including:
Centralized OPF with and without batteries ( time-steps).
Distributed* OPF with and without batteries. ( Areas)
*Spatially Distributed Computation, Brute-forced Temporal Computation.
Previous: Distributed OPF with batteries in a greedy “minimize losses right this time-period, for every time-period” manner. ( Areas, time-steps)

## Slide 25: Results: Boundary Variables
vs

## Slide 26: Results: Boundary Variables
vs

## Slide 27: Results: Boundary Variables
vs

## Slide 28: Current Status of Simulation and Results
SCD Plots to check Physical validity of Distributed MPOPF
This simulation was done for 5 time-steps (but the algorithm is scalable, and I’ve done them for 10, 15 time-steps. But the time taken by the brute force algorithm grows exponentially with number of time steps)
Charging and Discharging are always Complementary.
Terminal SOC is almost the same as initial SOC

## Slide 29: Current Status of Simulation and Results
Results for Node System from Centralized MPOPF
The plot shown is typical of the charging/discharging cycle for most batteries in the area.
This simulation was done for 5 time-steps (but the algorithm is scalable, and I’ve done them for 10, 15 time-steps. But the time taken by the brute force algorithm grows exponentially with number of time steps)
Charging and Discharging are always Complementary.
Terminal SOC is almost the same as initial SOC
IEEE Node System modelled here has nodes with Nodes and DERs and Batteries.

## Slide 30: Current Status of Simulation and Results
Results for Node System from Centralized MPOPF

## Slide 31: Thank You.

## Slide 32: Appendix and References follow

## Slide 33: Implementation Details
Platform, Input, Output
Platform:
Current Implementation is in MATLAB.
Model: Multi-Period Non-Linear OPF
Inputs:
Inputs are the same as Powerflow variables for a distribution system. That means: Topology:
busData: ,
branchData:
Power Demand Forecast Profile
PV Forecast Profile
PV Real Power/Reactive Power Limits
Battery Charging/Discharging Limits
Battery SOC Limits
What kind of objective function? Cost of Generation? Then give an estimate of Cost of substation power, cost of battery charging and cost of discharging power .
Outputs:
Optimal value of the objective function (say, line losses in or Cost of generation in ).
All state/control/output optimal variables. Such as: The nine optimization variables for all time instances across the horizon:
Output variables such as Substation Power .
Any other relevant variables.
Information needed to be exchanged between EDO Nodes and my area optimization controller. (depends on objective function)
Communication among OpenDSO nodes.

## Slide 34: Implementation Details
Optimization Algorithm Needs
Inputs: Data needs for Topology
Branch
  To Node, From Node, RX
Bus
  Controllable
    Base PQ
  Static Load PQ
    Allocation Factor
Devices
  Discover Buses and Branches for Section that it is optimizing
  Discover List of Upstream Neighbors and Downstream Neighbors
  Subscribe to their Parameters

## Slide 35: Implementation Details
Optimization Algorithm Needs
Inputs: Data needs from In Zone Devices
  Cap Bank
    Status
    Simple Expected Behavior
      Discussion: Need to establish a method to correlate measurements and model with expected controls actions.
  Regulator
    Tap Position
    Simple Expected Behavior
    Discussion: Need to establish a method to correlate measurements and model with expected controls actions.
Other Measurement Devices Data Needs
  For Static Load Calibration
  Solution Feedback

## Slide 36: Implementation Details
Optimization Algorithm Needs
Inputs: Data needs from Neighbor Algorithm Agents on OpenDSO
Power Flow
  V,I,P,Q
Algorithm Specific Coordination Parameters
  To be determined in algorithm system design
Convergence Indication
Speed of communication for iterative algorithm convergence
  Asynchronous vs Synchronous
  To be determined in algorithm system design

## Slide 37: Bounds and Values
Battery State/Control Variables (1/2)

## Slide 38: Bounds and Values
Battery State/Control Variables (2/2)

## Slide 39: Bounds and Values
BFM and DER State/Control Variables

## Slide 40: Reference of Notation: Battery Variables

## Slide 41: Reference of Notation: BFM and DER Variables

## Slide 42: Reference of Notation: Grid-level Notation
Helpful for clarifying any variable in the optimization formulations.

## Slide 43: Reference of Notation: Branch Flow Model and DER variables
Helpful for clarifying any variable in the optimization formulations.

## Slide 44: (IEEE 123 System divided into) 4 Area System

## Slide 45: [In development] Simulation Process of Spatially and Temporally Decomposed OPF algorithm.
Start
------------------------------------------------------------------------
Known:
-----------------------------------------------------------------------
while “temporal boundary variables are NOT equal in value for all consecutive time intervals”
  while “spatial boundary variables are NOT equal in value for all connected parent-child areas”
    Run (D-)OPF for minimizing the losses across the horizon for each area, in parallel. This is called as a macro-iteration.
    Exchange spatial boundary variables between all sets of connected parent-child areas.
    end
    Exchange temporal boundary variables between consecutive time intervals
end
------------------------------------------------------------------------
Stop

## Slide 46: Optimization Formulation
Mixed-Integer Non-linear Optimization Problem (in built-complementarity, but harder to solve)
Line Losses
Real Powerflow from a bus into the network
Reactive Powerflow from a bus into the network
Kirchhoff's Voltage Law (KVL)
Current Magnitude in a branch
Battery State of Charge Equation (this equation is temporally coupled, or has ‘memory’)
Complementarity of Charging and Discharging during a particular time interval.
DER Generation (forecasted, non-controllable)
Loads (forecasted, non-controllable)

## Slide 47: References
[1] Sadnan, R., & Dubey, A. (2021). Distributed Optimization Using Reduced Network Equivalents for Radial Power Distribution Systems. IEEE Trans. Power Syst., 36(4), 3645–3656. doi: 10.1109/TPWRS.2020.3049135
[2] Eilyan Bitar's Papers. (2023, August 16). Coordinated Aggregation
of Distributed Demand-Side Resources Pg 34. Retrieved from https://bitar.engineering.cornell.edu/papers.html
[3] Pandey, A., Agarwal, A., & Pileggi, L. (2020). Incremental Model Building Homotopy Approach for Solving Exact AC-Constrained Optimal Power Flow. arXiv, 2011.00587. Retrieved from https://arxiv.org/abs/2011.00587v1