## Slide 1: Scalable Multi-Period Optimal Power Flow for Active Power Distribution Systems or simply, Scalable MP-OPF in ADS
Aryan Ritwajeet Jha
Graduate Research Assistant
Washington State University
Notes: Remember to hit the reset button to make sure all the page elements react properly.
There are 20 different layouts that you can choose from.

## Slide 2: New MPOPF Implementation Progress
‘New’ because now it is being done in a new codebase which:
  Is easy to work with, is simple to modify and debug
  Uses OpenDSS .dss files for modelling all components
  (To do) Post Optimization uses OpenDSSDirect to verify optimization simulation.
ADS_ph with Loads, PVs and Batteries

## Slide 3: ADS_ph: MPCOPF Run for
MPCOPF Simulation Results
OpenDSS Powerflow Results
OpenDSS Def Profiles
Substation Power Cost
strLoadShapeCost = 'New Loadshape.LoadShapeCost npts =5 interval = 1 mult = [0.048204 0.048204 0.30181 0.30181 0.048204]'
Timings
Objective
Currently implementing OpenDSS verification scripts…

## Slide 4: ADS_ph: MPCOPF Run for
OpenDSS Def Profiles
Substation Power Cost
strLoadShapeCost = 'New Loadshape.LoadShapeCost npts =5 interval = 1 mult = [0.048204 0.048204 0.30181 0.30181 0.048204]'

## Slide 5: DDP for MPOPF for ADS Workflow

## Slide 6: DDP for MPOPF for ADS Workflow

## Slide 7: Latest Slides End Here. Previous Slides Follow.

## Slide 8: New MPOPF Implementation Progress
Currently converging .. to a non-sensible solution (zero substation power)
Hmm no reason for no GED load node 3 to have power backflow
Of course, SCD is also there.
Current thoughts: Bad sign in constraints? Bad per-unit-ization of a parameter?
Also checking out the constraints used

## Slide 9: Steps towards understanding Temporal Decomposition – Which Papers to Read?
Find work where it has actually been used.
  Beginning with only those which solve for the MPOPF problem.
    Right now, Transmission systems are OK too (they have to deal with ramping up/down constraints for generators)
    But may look into other domains as well afterwards
  Ascertaining which approach to follow, based on certain desirable features the future algorithm should have.

## Slide 10: Steps towards understanding Temporal Decomposition – Intended Algorithmic Solution
  Desirable features the future algorithm should have:
    Should be scalable with respect to Time (horizon duration)
      At least, something like time-steps should be solvable in one go
    Should ideally solve for the ‘true’ nonlinear problem, with as few approximations as possible
    Relaxations however are fine, and if they’re used, their solutions will obviously be checked for any infeasibility.
    Changing optimization formulation is undesirable for me. Something close to, if not exactly the same as the ‘standard’ nonlinear Branch Flow Model [farivar2013] is what I want.
      So, I’m looking to solve the problem using Branch Flow Variables only.
      Many papers, bring out their own new set of variables, approximations, customized algorithms to deal with them, in order to solve for the MPOPF problem. This is NOT what I’m looking to do.

## Slide 11: Do others ‘scalably’ solve MPOPF? – Some of them, Yes.
  These days, many papers pose a solution to the MPOPF problem.
    Many papers don't actually solve the problem in a scalable manner: the test-cases are reasonable (moderate sized, moderate penetration, day-ahead or large sized, low penetration, some hours only), but even they acknowledge that this formulation is not scalable, unless ...
    … Approximations are made

## Slide 12: How do others ‘scalably’ solve it? – Linearized Solution, Iteratively Improved
    Specifically,
    … Approximations are made at the most modular form of OPF formulation [usman2022, usman2023] which itself could be within a loop, where some meta-parameters are adjusted based on successive iterative updates.
      Some papers model these successive iterative updates on a homotopy based paradigm [agarwal2022]
MILP call inside a bigger algorithm
Some homotopy thing

## Slide 13: How do others ‘scalably’ solve it? – Hierarchical Optimization, Approximated (Relaxed) Top Level Step
    Specifically,
    The full optimization problem is divided into hierarchies, with the top hierarchy problem solving for an approximate (relaxed) model of the full horizon MINLP (NLP) problem.
    Once the top-level problem is solved and set-points for temporally-coupling decision variables are obtained, the same decision variables are kept as constant for every single time-step’s OPF formulation.
    The now temporally-decoupled Single-Period Optimal Power Flow Problems are formulated as SOCP (NLP) in a parallel manner.
    [nazir2018 (nazir2020)]
Inner SOCP call within an outer MILP loop
Inner NLP call within an outer SOCP loop

## Slide 14: How do others ‘scalably’ solve it? – Some sort of Algorithms involving Primal Dual Decomposition of the Constraints containing Variables from different time-steps
  Not fully appreciated (understood) by me yet. But here are two instances:
  In [agarwal2022] Their transmission system has many kinds of constraints, but only two temporally coupling constraints – Generator Ramping (one upper bound inequality and one lower bound inequality for each generator for each ‘time-boundary’) and Battery SOC (one equality for each battery for each time-boundary). All other equality/inequality constraints are constraints within a particular time-step, and thus are also called as uncoupled constraints.
  They then formulate a Lagrangian Function for the full OPF problem. After grouping ‘like’ terms together (as in whether they are temporally coupled or uncoupled), they ended up with this equation, which has (a summation of) temporally coupled terms (which come arise from the three kinds of temporal constraints) and temporally uncoupled terms (all contained in the first term)
  Finally, from the full horizon problem, a -th time-step problem function is carved out, which, outside the variables for that time-step, only contains certain primal and dual variables outside the time-step, including:
    (both lower and upper bounds),
Generator Ramping Constraints
Battery SOC Constraint
Lagrangian Function representing the full MPOPF problem (all time-steps)
Lagrangian Function representing the OPF problem for the -th time-step. Notice that the ‘new’ blocks are just terms from the ‘existing’ blocks but coming from the adjacent time-steps to

## Slide 15: How do others ‘scalably’ solve it? – Some sort of Algorithms involving Primal Dual Decomposition of the Constraints containing Variables from different time-steps
  Finally, from the full horizon problem, a -th time-step problem function is carved out, which, outside the variables for that time-step, only contains certain primal and dual variables outside the time-step, including:
    Past Primal Variables:
    Future Dual Variables: (both lower and upper bounds),
    While the problem itself cannot be solved for without knowing both past and future variables, as part of their Differential Dynamic Programming (DDP) Paradigm, they do a Forwards Pass and a Backwards Pass, wherein in each pass, they assume one set of variables to be constant (initially guessed, or possibly known from a previous computation).
Lagrangian Function representing the OPF problem for the -th time-step.

## Slide 16: How do others ‘scalably’ solve it? – Some sort of Algorithms involving Primal Dual Decomposition of the Constraints containing Variables from different time-steps
      Past Primal Variables:
      Future Dual Variables: (both lower and upper bounds),
    Specifically, in Forward Pass, they use the solved-for values of the past primal variables i.e. from the -th step as knowns for the problem at the -th step, and assume the last-known/initially-guessed values of the dual variables from the future i.e. from the -th step as constants, in order to fully solve the problem at the -th step.
    Once the values of the primal variables values for the -th step is known, they proceed one step forward, this time using those as the values of the past primal variables, again assuming the future dual variables as some constants.
    This forward pass process continues till the end-of-horizon (last time-step, let’s call it ).
Lagrangian Function representing the OPF problem for the -th time-step.
Scheme for Forward Pass and Backward Pass (here called ‘Sweep’ with no difference)

## Slide 17: How do others ‘scalably’ solve it? – Some sort of Algorithms involving Primal Dual Decomposition of the Constraints containing Variables from different time-steps
      Past Primal Variables:
      Future Dual Variables: (both lower and upper bounds),
  Once a forward pass is completed, i.e. the cost of the forward trajectory is constructed. It is time to solve for the gradients that will update the dual variables for the next forward pass.
  Thus after computation of these gradients, the next set of dual variables is computed.
  The process of Forward Pass and Backward Pass updates is carried on until convergence is achieved (updates no longer being significant).
Equations used for updating the future dual variables as part of the Backward Pass
Lagrangian Function representing the OPF problem for the -th time-step.
Scheme for Forward Pass and Backward Pass (here called ‘Sweep’ with no difference)

## Slide 18: How do others ‘scalably’ solve it? – Some sort of Algorithms involving Primal Dual Decomposition of the Constraints containing Variables from different time-steps
  Thus after computation of these gradients, the next set of dual variables is computed.
  The process of Forward Pass and Backward Pass updates is carried on until convergence is achieved (updates no longer being significant).
Done: I’ve understood the overall structure of a DDP implementation. Specifically, I’ve understood what is known, what is solved for, and what is assumed constant within a single time-period’s OPF. I understand the ‘Forward Pass’ component.
Current: I’m still studying the derivation required to understand the ‘Backward-Pass’ (how to use the gradient of the Lagrangian to get the dual variable updates). Once that is understood, I’ll have the understanding of one way to temporally decouple MPOPF for my use-case (ADS) as well, in a manner which can be implemented in code.
Equations used for updating the future dual variables as part of the Backward Pass
Lagrangian Function representing the OPF problem for the -th time-step.
Scheme for Forward Pass and Backward Pass (here called ‘Sweep’ with no difference)

## Slide 19: How do others ‘scalably’ solve it? – Some sort of Algorithms involving Primal Dual Decomposition of the Constraints containing Variables from different time-steps
  A paper utilizing ADMM for temporal decomposition: [pinto2020]
  Deficiencies:
    I don’t understand how ADMM works, because I don’t understand how dual variables work.
    To have a good understanding of dual variables, I have been reading up on theory [wolf2011]. I’ve gained some confidence in it but am yet to understand certain other key concepts thoroughly.
  The plan is to understand dual variables [wolf2011]., understand ADMM, understand ADMM usage in OPF [peng2015] , ultimately understand ADMM in MPOPF [pinto2020]
  .

## Slide 20: A Novel Tractable Methodology to Stochastic Multi-Period AC OPF in Active Distribution Systems Using Sequential Linearization Algorithm
Muhammad Usman, Member, IEEE, and Florin Capitanescu, Member, IEEE
IEEE TRANSACTIONS ON POWER SYSTEMS, VOL. 38, NO. 4, JULY 2023
Shortened as
SMPOPF in ADS using SLA – Usman, Capitanescu
PostDoc (now at National Grid ESO); Senior Researcher at
Luxembourg Institute of Science and Technology (LIST), Luxembourg

## Slide 21: One Page Overview
They model an ADS Grid with many kinds of components as an MINLP Problem (initially, for benchmarking)
They linearize the nonlinear terms of model using Taylor’s Second Order Approximation into an MILP model
They then use a Sequential Linearization Algorithm (SLA) approach which successively improves the accuracy of the MILP model in an iterative manner.
They showcase the efficiency of their algorithm for day-ahead, hourly planning on small/medium radial and weakly-meshed systems such as IEEE, UK, Portuguese with caveats on feasibility error.
SMPOPF in ADS using SLA – Usman, Capitanescu

## Slide 22: Overview of Paper - Modelling
They model an ADS Grid with many kinds of components, including:
  Flexible Loads Renewable Energy Sources (RES) with reactive power and scope of curtailment
  (FL) with overloading/ underloading
  Electrical Energy Storages (EES) (without reactive power)
  On Load Tap Changer Transformers (OLTC)
  as an MINLP Problem (initially, for benchmarking) which they label as
SMPOPF in ADS using SLA – Usman, Capitanescu

## Slide 23: Overview of Paper - Modelling
SMPOPF in ADS using SLA – Usman, Capitanescu
All component control functions have some cost associated with them.
Objective: Minimize the cost of network operations. cost of controlling ADS components, including FLs, RESs, EESs, OLTCs.

## Slide 24: Numerical Results
Three systems:
  IEEE bus radial ADS
  UK bus weakly-meshed ADS
  Portuguese bus radial ADS
  Horizon: hours (hourly-time period)
  Uncertainty Scenarios of solar and wind DERs
SMPOPF in ADS using SLA – Usman, Capitanescu

## Slide 25: Numerical Results
Three systems:
  IEEE bus radial ADS
  UK bus weakly-meshed ADS
  Portuguese bus radial ADS
  Horizon: hours (hourly-time period)
  Uncertainty Scenarios of solar and wind DERs
    PVs are less variable
    Wind profile is pretty variable.
SMPOPF in ADS using SLA – Usman, Capitanescu
PV Scenarios
Wind Scenarios

## Slide 26: Flexibility Options (FOs)
FO1: Active Power Curtailment (APC). (APC-FO1)
FO2: APC + OLTC
FO3: APC + Adaptive Power Factor (APF-FO3)
FO4: APC + APF + OLTC
FO5: APC + EESs
FO6: APC + FLs
FO7: APC + EESs + FLs
FO8: APC + EESs + FLs + APF
FO9: APC + EESs + FLs + APF + OLTC
SMPOPF in ADS using SLA – Usman, Capitanescu

## Slide 27: Parameters
Maximum Inner-Loop Iterations:
Maximum Outer-Loop Iterations:
Trustable Approximation Criterion: error value (between non-linear MPOPF and its linear approximation)
to switch to trust region path in the inner-loop.
AC Feasibility threshold (i.e. Nodal voltage/Branch current violation above is considered infeasible)
Benchmark MINLP solved via BONMIN (ratio gap = , allowable gap = )
Proposed MILP Model solved via CPLEX
Modelling for both models done in Julia/JuMP environment.
SMPOPF in ADS using SLA – Usman, Capitanescu

## Slide 28: Network being tested on
Current problem statement
  Test Case: IEEE123 Node System with Distributed Energy Resources (DERs) and Batteries.
  Balanced three-phase (with no phase coupling, akin to single-phase) power distribution network.
  Objective: Solve for Optimal Power Flow (OPF) for a horizon time interval of for a given objective function, say loss minimization.

## Slide 29: Network being tested on
ENApp Approach [1]
  Divide the network into several areas to solve for their Optimal Power Flow solutions separately, with exchange of boundary variables after every ‘macro-iteration’.
A previous model of the test system. Currently the system has DERs and Batteries on of the nodes with non-zero loads.

## Slide 30: Overall Scope of the problem Algorithm and Communication Architecture
OpenDSO-System Operator (Forecast)
OpenDSO-Measurement Devices
OpenDSO-EDO
OpenDSO-OpenDSO

## Slide 31
A simpler schematic for D-OPF.

## Slide 32
A simpler schematic for MP-D-OPF for three time-steps
(

## Slide 33
What is currently being done? MP-DOPF in Brute Force

## Slide 34
What is will be done? A ‘true’ MP-DOPF using Differential Dynamic Programming (Currently under formulation, variables not explained here) [20b]

## Slide 35: Multi-Period D-OPF simulation of a grid with DERs and Battery Storage

## Slide 36: Problem Statement
  Given the State of Charges of all batteries in a grid at the beginning of a horizon interval ( representing the set of nodes with Batteries, along with predictions for other non-controllable parameter values like :
  Solve for Optimal Power Flow of the system, with the objective of minimizing line losses across the entire horizon of time interval

## Slide 37: Problem Statement
  Given the State of Charges of all batteries in a grid at the beginning of a horizon interval ( representing the set of nodes with Batteries, along with other non-controllable parameter values like :
  Solve for Optimal Power Flow of the system, with the objective of minimizing line losses across the entire horizon of time interval
  while making sure that:
  1. (the SOC of the battery at every point of the simulation) stays in permissible limits
  2. The OPF Solution is physically consistent. For no node containing a battery, is . In other words, make sure that Complementarity of Discharging and Charging is ensured. Alternatively, Simultaneous Charging and Discharging (SCD) is avoided.
  3. Other usual OPF physical constraints are also satisfied.
  4. Terminal SOC is same as initial.

## Slide 38: Simulation Parameters
Objective: Minimize Line Losses
System: IEEE Node System
Phase: Balanced
Supply: DERs and Batteries at select (about of total) nodes. Substation.
Demand: Flat line (will be made varying each time-step in future simulations)
Control: Inverter Reactive Power Control for DERs and Batteries. Battery Charging/Discharging.
Number of discrete time-steps:
Duration per time-step: .

## Slide 39: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: BFM Constraints with Battery and DER decision variables.
Line Losses
Real Powerflow from a bus into the network
Reactive Powerflow from a bus into the network
Kirchhoff's Voltage Law (KVL)
Current Magnitude in a branch

## Slide 40: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: BFM Constraints with Battery and DER decision variables.
Line Losses
DER Inverter Reactive Power
Nodal Voltage Limits

## Slide 41: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: BFM Constraints with Battery and DER decision variables.
Line Losses
Battery State of Charge Equation (this equation is temporally coupled, or has ‘memory’)

## Slide 42: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: BFM Constraints with Battery and DER decision variables.
Line Losses
Battery SOC Permissible Limits
Battery Inverter Reactive Power Limits
Battery Charging and Discharging Power Limits

## Slide 43: Optimization Formulation
(Integer-Constraint Relaxed) Non-linear Optimization Problem: Tweaking the Objective Function to satisfy some more constraints.
Line Losses
Ensures Complementarity of Charging and Discharging, or alternatively, ensure there’s no SCD.
For minimizing the deviation between end-of-day battery SOC and a reference SOC.

## Slide 44: Optimization Formulation
(Integer-Constraint Relaxed) The Full Non-linear Optimization Problem
Real Powerflow from a bus into the network
Reactive Powerflow from a bus into the network
Kirchhoff's Voltage Law (KVL)
Current Magnitude in a branch
#Types of variables
#Variables
#Equality Constraints
(Non-Linear)
DER Generation (forecasted, non-controllable)
Loads (forecasted, non-controllable)
Line Losses
Ensures Complementarity of Charging and Discharging, or alternatively, ensure there’s no SCD.
For minimizing the deviation between end-of-day battery SOC and a reference SOC.
Battery State of Charge Equation (temporally coupled) with complementarity relaxed.

## Slide 45: Current Status of Simulation and Results
What has been done
A variety of simulation runs have been modelled and run for the sake of benchmarking including:
Centralized OPF with and without batteries ( time-steps).
Distributed* OPF with and without batteries. ( Areas)
*Spatially Distributed Computation, Brute-forced Temporal Computation.
Previous: Distributed OPF with batteries in a greedy “minimize losses right this time-period, for every time-period” manner. ( Areas, time-steps)

## Slide 46: Results: Boundary Variables
vs

## Slide 47: Results: Boundary Variables
vs

## Slide 48: Results: Boundary Variables
vs

## Slide 49: Current Status of Simulation and Results
SCD Plots to check Physical validity of Distributed MPOPF
This simulation was done for 5 time-steps (but the algorithm is scalable, and I’ve done them for 10, 15 time-steps. But the time taken by the brute force algorithm grows exponentially with number of time steps)
Charging and Discharging are always Complementary.
Terminal SOC is almost the same as initial SOC

## Slide 50: Current Status of Simulation and Results
Results for Node System from Centralized MPOPF
The plot shown is typical of the charging/discharging cycle for most batteries in the area.
This simulation was done for 5 time-steps (but the algorithm is scalable, and I’ve done them for 10, 15 time-steps. But the time taken by the brute force algorithm grows exponentially with number of time steps)
Charging and Discharging are always Complementary.
Terminal SOC is almost the same as initial SOC
IEEE Node System modelled here has nodes with Nodes and DERs and Batteries.

## Slide 51: Current Status of Simulation and Results
Results for Node System from Centralized MPOPF

## Slide 52: Conclusion and Discussion
Major Observations:
Batteries were modelled correctly, i.e. no Simultaneous Charging and Discharging was observed.
Terminal SOC values (SOC values at end of day) mostly kept close to the original SOC values (beginning of day).

## Slide 53: Bounds and Values
Battery State/Control Variables (1/2)

## Slide 54: Bounds and Values
Battery State/Control Variables (2/2)

## Slide 55: Bounds and Values
BFM and DER State/Control Variables

## Slide 56: Reference of Notation: Battery Variables

## Slide 57: Reference of Notation: BFM and DER Variables

## Slide 58: Reference of Notation: Grid-level Notation
Helpful for clarifying any variable in the optimization formulations.

## Slide 59: Reference of Notation: Branch Flow Model and DER variables
Helpful for clarifying any variable in the optimization formulations.

## Slide 60: (IEEE 123 System divided into) 4 Area System

## Slide 61: [In development] Simulation Process of Spatially and Temporally Decomposed OPF algorithm.
start
------------------------------------------------------------------------
Known:
-----------------------------------------------------------------------
while “temporal boundary variables are NOT equal in value for all consecutive time intervals”
  while “spatial boundary variables are NOT equal in value for all connected parent-child areas”
    Run (D-)OPF for minimizing the losses across the horizon for each area, in parallel. This is called as a macro-iteration.
    Exchange spatial boundary variables between all sets of connected parent-child areas.
    end
    Exchange temporal boundary variables between consecutive time intervals
end
------------------------------------------------------------------------
stop

## Slide 62: Optimization Formulation
Mixed-Integer Non-linear Optimization Problem (in built-complementarity, but harder to solve)
Line Losses
Real Powerflow from a bus into the network
Reactive Powerflow from a bus into the network
Kirchhoff's Voltage Law (KVL)
Current Magnitude in a branch
Battery State of Charge Equation (this equation is temporally coupled, or has ‘memory’)
Complementarity of Charging and Discharging during a particular time interval.
DER Generation (forecasted, non-controllable)
Loads (forecasted, non-controllable)

## Slide 63: Multi-Period D-OPF simulation of a grid with DERs and Battery Storage
Naïve Brute-Force approach to MPOPF being implemented (Solve for the full problem for the full horizon in one go).

## Slide 64: Optimization Formulation
The Full Optimization Problem for Brute-Force MPOPF
#Types of variables
#Variables
#Equality Constraints
(Non-Linear)

## Slide 65: Optimization Formulation
The Full Optimization Problem for Brute-Force MPOPF
#Types of variables
#Variables
#Equality Constraints
(Non-Linear)

## Slide 66: Optimization Formulation
The Full Optimization Problem
Fixed values accounted for into .
#Types of variables
#Variables
#Equality Constraints
(Non-Linear)
SCD Term (Green Box)

## Slide 67: Optimization Formulation
The Full Optimization Problem: Linear Objective, Non-Linear Constraint
Fixed values accounted for into .
#Types of variables
#Variables
#Equality Constraints (Non-Linear)
Most Complicated Scenario Possible
Will happen when every node has a DER and a Battery
SCD Term (Green Box)

## Slide 68: Optimization Formulation
The Full Optimization Problem: Linear Objective, Non-Linear Constraint
#Types of variables
#Variables
#Equality Constraints (Non-Linear)
Most Complicated Scenario Possible
Want to start with a good initialization for all state/control variables.
So should solve for some ‘simpler’ Optimization Problems.

## Slide 69: Optimization Formulation
Making a simpler Optimization Problem
#Types of variables
#Variables
#Equality Constraints (Non-Linear)
Most Complicated Scenario Possible
Start with removing some terms form the problem.
We hope to get good initialization values for the more complex problems.
Typo. Signs are flipped.
Typo: Times are actually and instead of and

## Slide 70: Optimization Formulation
Making a simpler Optimization Problem
#Types of variables
#Variables
#Equality Constraints (Non-Linear)
Most Complicated Scenario Possible
Class of Variable | Reason for Ignoring
 | Removing Losses makes model linear.
 | Side effect of the combined effect of current SCD term and type of objective function. Not including the Green Box Term can cause SCD. But adding the Green Box term without any loss term in the objective function basically penalizes any kind of battery participation.
Current/Loss Term
Battery Variables
Typo. Signs are flipped.
Typo: Times are actually and instead of and

## Slide 71: Optimization Formulation
Initialization Step 1a: Feasibility on Linear Constraints
#Types of variables
#Variables
#Equality Constraints (Linear)
Get feasible values of

## Slide 72: Optimization Formulation
Initialization Step 1a: Feasibility on Linear Constraints
#Types of variables
#Variables
#Equality Constraints (Linear)
Most Complicated Scenario Possible
Get feasible values of

## Slide 73: Optimization Formulation
Initialization Step 1b: Quadratic Objective, Linear Constraints
#Types of variables
#Variables
#Equality Constraints (Linear)

## Slide 74: Optimization Formulation
Initialization Step 1b: Quadratic Objective, Linear Constraints
#Types of variables
#Variables
#Equality Constraints (Linear)
A ‘fake’ line-loss function. We don’t want to involve already as we’re yet to get good initialization for any of the Battery Variables.
We use results from Initialization Step . We can’t involve as an optimization variable as that would make the ‘fake’ loss minimization function non-convex.

## Slide 75: Optimization Formulation
Initialization Step 1b: Quadratic Objective, Linear Constraints
#Types of variables
#Variables
#Equality Constraints (Linear)
Most Complicated Scenario Possible

## Slide 76: Bounds and Values
Battery State/Control Variables

## Slide 77: Bounds and Values
– The Coefficient for the Green Box term penalizing SCD

## Slide 78: Results: Real Power Losses
vs
While batteries have charge to spare, the losses are minimized, as less power needs to flow all the way from the substation.
Here, for the first time-periods, or , the batteries are able to discharge at their maximum capacity, and so the line losses are significantly lower. By time-periods, they completely run out of SOC (reach minimum value of SOC), and the losses return to ‘normal’, pre-battery configuration.

## Slide 79: A metric for quantifying effect of storage and DER power on the grid.
More savings in losses and substation power through batteries.
Power flowing into the area indirectly via the substation (directly for Area 1).
Solar generated power for the whole area.
Net real power injected into the area via batteries.

## Slide 80: Results: Reactive Power Losses
vs
Investigate further. I thought that since batteries don’t generate Real Power when they run out of SOC, they should generate more reactive power. I guess more real power flow is highly coupled with more reactive power flow? Need to check values.

## Slide 81: Results
vs
Machine dependent AND still varies every run.
My personal machine
My Lab machine
To do: Clarify the values in the plot and the ones in the logs. How exactly are they different again?

## Slide 82: Results
vs

## Slide 83: Results: Boundary Variables
vs
Investigate: Negative Reactive Power Flowing from Area 1 to Area 3 and Area 2 to Area 4? Check reactive generation values for the areas.
As expected.

## Slide 84: Results: Battery Variables
, vs
This plot is for one battery, specified by an Area and Node (for that area).
The plots for other batteries are near identical, as only SOC percentages have been plotted instead of absolute battery charge in
Batteries initially discharge at maximum rate, which helps in:
Loss Minimization
Voltage Deviation Minimization (not explicitly solved for, but noted from the plots of node voltages)
until they reach their minimum permissible SOC.
Zero charging. (will plot together later to clearly highlight that)

## Slide 85: Results
Simulation went in an intuitive manner.
Batteries ONLY discharged. They kept discharging until their State of Charge dipped to the minimum permissible value of , i.e.
. This is intuitive, as for a greedy minimization of line-losses with no perspective of any future opportunity costs for not being able to discharge, the batteries have no incentive to charge, and all the incentive to discharge.
Other variables depend on the above fact. For the first time-periods ( of simulation-time), while the batteries haven’t run out of charge, line losses , Substation Power are kept significantly lower, and savings due to batteries is high for every area. By the time-periods, soar to ‘battery-less’ levels, an drops to a low, constant value.
Multi-Period D-OPF of IEEE Node System

## Slide 86: Takeaways
Handle SCD (Green Box) term with care.
While it has helped us relax the constraint of Boolean Variables in the optimization modelling and solving, it needs extra caution for modelling in order to arrive at a useful solution.
For example, it cannot be used alone without the main objective function, such as loss minimization. Otherwise, the optimizer will penalize any participation of the batteries, making both and for all batteries.
needs to be carefully designed. The value of the SCD Green Box should be within a magnitude range of the line loss function’s value. Too greater, and it would reduce battery power to zero, too low, and SCD might occur.
The cost of replacing the Boolean Constraints with the SCD Green Box term for avoiding SCD.

## Slide 87: Takeaways
However, if we use an economic based model, which assigns a cost to substation power and battery charging/discharging, then the number of optimization steps can be reduced to just two, with one initialization with no line losses, as is a state variable itself which does not require any other non-linear equality constraint term like .
But in that case, we need to clarify who owns the storage (cite that paper), as the coefficient for cost function of battery charging/discharging could then be either positive or negative (how?).
The cost of replacing the Boolean Constraints with the SCD Green Box term for avoiding SCD.

## Slide 88: Reference of Notation

## Slide 89: Reference of Notation
Helpful for clarifying any variable in the optimization formulations.

## Slide 90: Battery Models Used in Various Papers
Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Ensures Complementarity (i.e., ensures absence of SCD) without any additional boolean constraints.
They prefer rectangular coordinates for all complex variables, for usage in Newton Raphson method.
SOC is always taken as energy (base )

## Slide 91: Battery Models Used in Various Papers
Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations

## Slide 92: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Optimization Loops (Time-scales): An ‘Outer’, slower MILP loop for fixing battery SOC values and STL element values.
An ‘Inner’, faster SOCP loop for solving for optimal power flows.
Battery apparent power (through inverter) limits.

## Slide 93: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Optimization Loops (Time-scales): An ‘Outer’, slower MILP loop for fixing battery SOC values and STL element values.
An ‘Inner’, faster SOCP loop for solving for optimal power flows.
Battery apparent power (through inverter) limits.

## Slide 94: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Upon addition of the green block, the grey terms are removed from the constraints.
The yellow block ensures that the terminal battery SOC value (i.e. SOC value at the end of the horizon) prescribed by the outer loop is adhered to.
is also an optimization (control) variable

## Slide 95: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations

## Slide 96: Battery Models Used in Various Papers
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations
For a system WITHOUT any STL elements, instead of a (MI , SOCP) loops, they use (SOCP, NLP) loops.
Battery models themselves are the same.
Also, NO yellow term this time.

## Slide 97: Battery Models Used in Various Papers
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations
For a system WITHOUT any STL elements, instead of a (MI , SOCP) loops, they use (SOCP, NLP) loops.
Battery models themselves are the same.
Also, NO yellow term this time.

## Slide 98: Battery Models Used in Various Papers
Battery Dispatching for End Users With On-Site Renewables and Peak Demand Charges – An Approximate Dynamic Programming Approach
Initial thoughts: It uses a linear/linearized model of the battery, and all equations are expressed with matrices.
Details to be added later.

## Slide 99: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Xiaodong Qian and Yuanguo Zhu
Seventh International Joint Conference on Computational Sciences and Optimization (2014)
Deptt. Of Appl. Math.
Nanjing University of Science and Technology (NUST)
Professor with the Department of Mathematics
NUST, Nanjing, China
Has 1 citation – by the SUGAR-DDP paper by Agarwal and Pileggi

## Slide 100: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Starting with an expression for the Cost-to-go function for an Uncertain Optimal Control Problem.

## Slide 101: Differential Dynamic Programming for Multistage Uncertain Optimal Control
In about equations, it provides an algorithm for solving a stochastic MPC problems using Differential Dynamic Programming (DDP). It initializes the solution using an unspecified Genetic Algorithm (GA).

## Slide 102: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Key equations required for Step 1 of the algorithm:

## Slide 103: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Key equations required for Step 2 of the algorithm:

## Slide 104: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Key equations required for Step 3 of the algorithm:
Given in another reference.

## Slide 105: Differential Dynamic Programming for Multistage Uncertain Optimal Control
At the end it also gives a numerical example utilizing the algorithm.

## Slide 106: Differential Dynamic Programming for Multistage Uncertain Optimal Control
It uses Genetic Algorithms for Initializing the solution.
Given in another reference.

## Slide 107: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Utilizing the key derived equations for the algorithm for this specific problem:

## Slide 108: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Utilizing the key derived equations for the algorithm for this specific problem:

## Slide 109: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Results are on the right.

## Slide 110: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Takeaway:
This paper provides a solid mathematical understanding of the rationale behind Differential Dynamic Programming.
It provides an algorithm along with a conveniently described set of equations which can aid us in solving our own problems using DDP.
Which are generated because we use Taylor’s Linear Approximations.

## Slide 111: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Aayushya Agarwal and Larry Pileggi
IEEE TRANSACTIONS IN POWER SYSTEMS (2022)
PhD student at Carnegie Mellon University (CMU)
Prof. at CMU
Reference papers with: Amritanshu Pandey Assistant Prof. at UVM

## Slide 112: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Objective function is economic-based
Charging/ Discharging cost considered
Charging/Discharging efficiency considered
Ramping of Active Power Generation form Synchronous Generators considered.

## Slide 113: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation
For a single time-period ACOPF, a Lagrange function with dual and slack variables is formed to represent network equality constraints and device limits respectively:

## Slide 114: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation
Where is a vector of dual variables associated with each equality constraint defined in [20b]
In the same reference, is a vector of inequality constraints representing generator active and reactive power limits, bus voltage bounds and line loading constraints with a vector of corresponding slack variables, .
Introduced in SUGAR: is a ‘feasibility current’ at each node and is minimized according to a large weight .
In a feasible optimal dispatch solution, all feasible current sources will be equal to .

## Slide 115: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation
Reference [20b] equations.

## Slide 116: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: Sugar ACOPF
SUGAR defines a set of the modified KKT conditions of representing the first order optimality conditions to ensure a local minimum is reached.
The non-linear KKT equations are solved for using Newton-Raphson.
Each iteration, the Newton-Raphson constructs a Hessian of the .

## Slide 117: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: SUGAR ACOPF – Diode Limiting
Inequality constraints are solved using an interior point method that gradually constrains the function shown in (9).
Each iteration of the interior point method requires robust limiting to ensure variables do not exceed their operating limits.
‘Diode limiting methods’ from [23b] ensure each primal variable and associated slack variable is individually limited, with a factor of and respectively (12-13).
(14-15) represent damping constants to ensure there’s no inter-iteration oscillation of primal/slack variables.

## Slide 118: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: SUGAR ACOPF – Tx-stepping based Homotopy Method
SUGAR accommodates arbitrary initial conditions by employing a homotopy method that relaxes the non-linear constraints to a trivial problem , and then sequentially solves a series of sub-problems to the original problem .
A scalar homotopy factor is embedded into the non-linear ACOPF formulation and is iteratively decreased from to to trace a path in the solution space.
They claim that this works for arbitrary initial conditions and shows robust convergence for ACOPF systems.

## Slide 119: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: Generator Ramping Limits
Generator ramping limits are incorporated in the same way and solved for using an interior-point method.
ESS also incorporated. (Didn’t see or read any explanation on the possibility of SCD, i..e )

## Slide 120: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: MP-OPF
How is Simultaneous Charging Discharging (SCD) avoided?

## Slide 121: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: MP-OPF
Augmented Lagrangian of the MP-OPF problem.

## Slide 122: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: MP-OPF
If not for any Generator ramping or ESS constraints, the problem is just a summation of individual ACOPFs.
The authors anyway proceed to solve for each ACOPF individually, but using a Forward-Backward Process.
While solving for time , they assume any variables from as some constants, and solve (‘forward-pass’) to get all variables for time-step .
Then they do a ‘backwards-pass’ to update the sequence based on gradient information from the forward trajectory.
Together, a forward pass and a backward pass produce a new sequence of controls.
If converged, the backward pass does not affect the forward trajectory.

## Slide 123: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Results: 14 Bus System
Gen 02 replaced with an Energy Storage System.
Optimized over 10 hourly time-periods.
Loading factor is the blue curve (min. 1.0, Max. 1.4)
Optimal solution: Charge during periods of low demand (1 to 3), discharge during high loading time (hours 3 to 9). Because discharging cost is much lower than cost of getting power from synchronous machines.
Still, ramping constraints of the synchronous machines restrict the battery from discharging its entire energy.

## Slide 124: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Results: 14 Bus System
Gen 02 replaced with an Energy Storage System.
Optimized over 10 hourly time-periods.
Loading factor is the blue curve (min. 1.0, Max. 1.4)
Optimal solution: Charge during periods of low demand (1 to 3), discharge during high loading time (hours 3 to 9). Because discharging cost is much lower than cost of getting power from synchronous machines.
Still, ramping constraints of the synchronous machines restrict the battery from discharging its entire energy.

## Slide 125: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Results: Synthetic 70k testcase

## Slide 126: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Results: Synthetic 70k testcase
Solving for 10 hours of 70k system data configuration took them 14 minutes on a single-core macbook.

## Slide 127: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Differential Dynamic Programming: Convergence Analysis
Using Hessians, Gauss-Seidel, spectral radius, positive-definiteness, they prove that for realistic systems, this method always works.

## Slide 128: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Nawaf Nazir and Mads Almassalkhi
Power System Computation Conference (2018)
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Nawaf Nazir, Pavan Racherla and Mads Almassalkhi
IEEE TRANSACTIONS IN POWER SYSTEMS (2020)
Reference [22]

## Slide 129: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Reference [22]
IEEE 123 and 13 bus systems
Unbalanced, Phases assumed to be NOT coupled
Second Order Conic Decomposition (SOCP) used to fix State-of-Charge (SOC) for batteries at every time step. [~1 minute]
Non-Linear Programming (NLP) to solve the individual decoupled time-steps (in parallel). [~ seconds]
Uses the proof on the based on the 2018 paper to assume a relaxation of the complementarity constraint (with suitable augmentation of the objective function).
IEEE 13 bus system
Unbalanced, Phases assumed to be NOT coupled.
STL Elements (Discrete-control)
Optimized slowly using Multi-Integer Linear Programming
Renewables + Battery
Optimized fastly using SOCP
[~1 minute]
Proof given, that for realistic systems, relaxing the hard battery complementarity constraint AND adding a soft constraint to the objective function, makes the problem NOT Mixed-Integer, while still yielding feasibly, near-optimal soltutions.

## Slide 130: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Nawaf Nazir and Mads Almassalkhi
Power System Computation Conference (2018)
Currently at PNNL Then: PhD at University of Vermont (UVM)
Currently Assoc. Prof. at UVM

## Slide 131: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Distribution System
  Unbalanced
  Mechanical Assets?
  Significant Solar Penetration
Two Different Optimization Time-Scales
  A slow time-scale for dispatching discrete mechanical assets using Mixed-Integer Program (MIP)
  A fast time-scale for continuously monitoring DERs using SOCP.

## Slide 132: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Different Optimization Time-Scales
  Different Types of discrete and continuous operated devices.
    E.g. Capacitor/Reactor Banks, Line Regulators (On/Off), Load-Tap-Changing (LTC) Transformers
    Discrete states of these devices render the problem NP-hard. (So, they were NOT NP-hard anyway?)
    McCormick relaxation and linearization techniques have been used to incorporate these devices into the OPF problem for a BALANCED network. [16b]
  This necessitates the use of separate optimization loops to coordinate them.
  Mechanical assets also have operational constraints on tap changes per hour to limit wear and tear, which necessitates separation.

## Slide 133: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Novel hierarchical OPF scheme for separation of the slow-mechanical (discrete control scheme) and fast power-electronic (continuous control scheme) on two different time-scales.
Service Transformer Layers (STL) elements dispatched optimally using Multi-Period three-phase SOCP convex relaxation techniques applied to radial distribution networks for fast corrective control.
Simultaneous charging and discharging of batteries in a convex model of 3-phase system is also analyzed and conditions are provided under which this can be avoided.

## Slide 134: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
AC Three-phase Non-Linear Model (Plant)
Minutely Dispatch of Flexible Assets (SOCP)
Hourly Dispatch of Mechanical Assets (MILP)
Forecast and Analytics
Flowchart showing the Hierarchical time-scale control algorithm

## Slide 135: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Want to minimize number of changes in mechanical discrete control components to reduce wear and tear.
  Aim: minimize from a nominal set-point using operation of these discrete assets.
  The outer loop also schedules active power exchanges of the STL elements, considering the variability of solar PV generation and forecast energy demands.
  Reactive Power Control of STL elements reserved for corrective control, in the Inner Loop.
Outer Loop Formulation: Voltage Positioning

## Slide 136: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Since discrete decision variables only take integer values, the outer loop problem becomes a mixed-integer problem, which is NP-hard.
  Branch and bound techniques can be effective on MIPs if their continuous versions are convex.
  In order to reduce the computational complexity of the outer loop, a three-phase LINEARIZED model of the network is used.
  This reduces the problem to a Mixed-Integer Linear Program (MILP).
Outer Loop Formulation : Voltage Positioning

## Slide 137: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  STL Architecture
    Four-Quadrant Control Scheme. Can supply and consume both and .
    Each STL element is composed of a renewable source of energy such as solar power and some form of storage like a battery bank.
Outer Loop Formulation : Voltage Positioning
Solar PV
Battery
Inverter
Inverter
Transmission Network.

## Slide 138: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Aim: minimize in the network.
    while keeping track of a power reference signal from the transmission level.
    while keeping the system within operational bounds.
  This program optimizes the STL elements over the fast time-scale.
  This corrective optimization loop is required to be fast ( minute).
  Three-phase SOCP used to solve the optimization problem.
    A Branch Flow Model (BFM) is used to represent the power flow equations.
Inner Loop Formulation: Corrective OPF

## Slide 139: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  The Inner Loop optimization problem can thus be formulated as:
  <INSERT formulae (26) to (36)>
    Inner Loop Objective function
    Power Balance Equation (BFM)
    Power Flow Equations (BFM)
    Line Power Flow Constraints
      Relation between BFM sub-matrices
    Voltage Constraint
    Solar PV Constraint
    Node Power Relations
    Battery State of Charge and Complementarity Constraints
Inner Loop Formulation: Corrective OPF

## Slide 140: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Complementarity: Charging and Discharging are complementary phenomenon for a battery, i.e. at NO time step, can a battery simultaneously undergo charging and discharging.
  Complementarity Constraints ensure that Batteries never charge and discharge simultaneously.
    But these constraints make the SOCP of the Inner Loop Non-Convex.
    One way to make it convex would be to use Mixed-Integer SOCP in the Outer Loop.
      But that would make increase the computation time substantially.
      We h0wever want solution time (to obtain a near-optimal solution) to be minute.
      So not doing that.
Relaxing Complementarity Constraint

## Slide 141: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Complementarity Constraints ensure that Batteries never charge and discharge simultaneously.
    But these constraints make the SOCP of the Inner Loop Non-Convex.
    One way to make it convex would be to use Mixed-Integer SOCP in the Outer Loop.
      But that would make increase the computation time substantially.
      We h0wever want solution time (to obtain a near-optimal solution) to be minute.
      Instead our approach is to relax these constraints and analyze the conditions where the optimal solution still respects them.
Relaxing Complementarity Constraint

## Slide 142: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
      Instead, their approach is to relax these constraints and analyze the conditions where the optimal solution still respects them.
      In [23b], [24b], authors provide conditions under which complementarity is satisfied in the optimal solution for an economic dispatch problem.
        In [24b], KKT conditions are analyzed for a DC model of an economic dispatch problem and they show that under realistic assumptions, complementarity is respected.
        In this paper, the analysis is extended to a distribution system setting where the objective is to minimize line losses, while considering four quadrant battery operation.
Relaxing Complementarity Constraint

## Slide 143: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
Inner Loop Formulation: Corrective OPF

## Slide 144: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
Inner Loop Formulation: Corrective OPF

## Slide 145: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
    Additional ‘loss functions’ for 1. Penalizing SCD and 2. Respecting Battery SOC Limits.
Inner Loop Formulation: Corrective OPF

## Slide 146: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
IEEE 13
Unbalanced
has 1-phase, 2-phase, 3-phase lines
A Three-phase OLTC transformer between 633 and 634
Capacitor Banks placed at 675 and 611
STL elements added at nodes 632, 675, 680, 684
  These STL elements each have:
    Solar PV generation
    Battery capable of four-quadrant operation.
Test Cases and Numerical Simulations
Modified IEEE 13 bus system used.

## Slide 147: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Nawaf Nazir, Pavan Racherla and Mads Almassalkhi
IEEE TRANSACTIONS IN POWER SYSTEMS (2020)
Currently at PNNL PhD at University of Vermont (UVM)
Currently Asst. Prof. at UVM
Currently Assoc. Prof. at UVM

## Slide 148: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Distribution System
  Unbalanced
  Inverter-Interfaced
  Significant Solar Penetration
Three-Phase Unbalanced
  Non-Convex Loss-minimization problem
  Formulated as a Convex Second Order Conic Program (SOCP) for arriving at an initial solution for Non-Linear Program (NLP)
  NLP run to ensure physically realizable solution

## Slide 149: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Conditions derived to ensure that batteries do NOT simultaneously charge and discharge. (Is that a big problem?)
Tested with GridLab-D for IEEE 13 and IEEE 123.
  AC feasibility of the solutions ensured
  Near-optimal performance
  Solution time < 1 min.

## Slide 150: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
ConEd* of NY moving towards Distributed System Platforms (DSPs)
These DSPs allow for DERs to be factored into Optimization schemes for Power Generation
DERs can be Optimized to function as Virtual Batteries (VBs)
  provide energy services at different spatio-temporal scales.
* Consolidated Edison, electric utility in NY and NOT ComEd, Commonwealth Edison, electric utility in IL

## Slide 151: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Traditionally, DistFlow algorithms based on the Branch Flow Model (BFM), which are an exact non-linear formulation of the distribution power flow equations, only work on balanced single-phase equivalent networks.
  But Distribution Networks are inherently unbalanced.

## Slide 152: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  In [22] by the same authors, they have developed a three-phase convex SOCP relaxation of the multi-period OPF problem, and provided sufficient conditions which ensure the avoidance of simultaneous charging and discharging.
  In this paper, they extend the work by developing a Multi-Period SOCP-NLP algorithm that provides a near optimal and guaranteed feasible solution.

## Slide 153: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  The optimized solutions from the relaxed SOCP model, are used to initialize a Non-Linear Program (NLP) of the actual AC Power Flow, to obtain a physically realizable solution.
  Real-Power Solutions that form the energy trajectory and are obtained from the SOCP, are fixed in the NLP, leading to a decoupling of the different time-steps. (What? How?)
  As a result, the NLP solves for each time-step separately (possibly in-parallel), leading to a scalable framework. (What?)
  Validation is performed using GridLab-D.

## Slide 154: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  IEEE , Unbalanced,
  Algorithm implemented in Receding-Horizon fashion.
  Receding-Horizon means a rolling window where predictions for the next time-steps from time to are made at time and since predictions are updated at every time step, for the next time step , predictions for the next time steps from to are once again made.
  The cycle goes on.
Fig. Aggregate solar, demand and net-demand profile over a prediction horizon of

## Slide 155: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
The SOCP solution outputs an optimal battery and inverter control schedule
The schedule is used by the NLP to calculate a physically realizable schedule
The physically realizable schedule is implemented by GridLab-D to determine the resulting AC Power Flows.
The forecast of demand and renewable generations are updated.
The Process

## Slide 156: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
The Process
Fig. Coupling of SOCP with NLP by fixing real power solutions from SOCP and hence decoupling the NLP to obtain a feasible solution. (What? How?)
Fig. Available reactive power variation range for NLP across multiple time-steps based on the active power trajectory provided by the SOCP.

## Slide 157: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  Distributed Storage and Solar PV Units randomly added to nodes
    They can supply active and reactive power through four quadrant operation.
    Each storage unit has capacity and apparent power rating
    Each solar PV unit has a rating
  Solar and Load Profile prediction horizon
    Each step

## Slide 158: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  Three-phase OPF is run in a receding horizon fashion with prediction horizon of time-steps, for the dispatch of controllable assets of the network to minimize network losses.
  Set-points provided by the solutions of the SOCP are used to initialize an NLP to provide a feasible solution.
    SOCP modeled in JuMP, with Julia and solved using GUROBI.
      Multi-period SOCP has
        kvariables (k as in thousand)
        k linear constraints
        k SOC constraints

## Slide 159: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
    NLP also modeled in JuMP, but solved using IPOPT [36] using the HSL_MA86 solver [37]
      A single-period of the Multi-period SOCP has
        kvariables
        k linear constraints
        k SOC constraints
        k non-linear constraints

## Slide 160: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
    levels for both loads (low and high) and solar PV generation (low and high)
    ‘High’ implies Base Values for both Loads as well as solar PV
    ‘Low’ implies of the base values in both cases.
    Thus scenarios are modeled:
      LL (Low Solar, Low Loads)
      LH (Low Solar, High Loads)
      HL (High Solar, Low Loads)
      HH (High Solar, High Loads)
Different Solar and Load Cases

## Slide 161: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Run 1: SOCP with NO Complementarity constraint added to objective function.
  Run 2: SOCP with Complementarity constraint added to objective function.
  Run 3: MI Problem which inherently solves with the Complementarity condition.

## Slide 162: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Run 1: Gives a Physically unrealizable solution.
  Run 2 and Run 3: Give the SAME feasible solution.

## Slide 163: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Run 2 and Run 3: Give the SAME feasible solution.
  Also, the SAME Optimal solution.

## Slide 164: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Optimality gap always below 3% for different solar penetration levels.
  Feasible solutions always ( difference).
  Solution times
  NLP total time assuming parallelized operation over every single time step.
Table: Comparison of the Optimality Gap Values of SOCP and NLP.

## Slide 165: References
[22] Nazir, N., & Almassalkhi, M. (2018). Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices. 2018 Power Systems Computation Conference (PSCC). IEEE. doi: 10.23919/PSCC.2018.8442555
[36] Wächter, A., & Biegler, L. T. (2006). On the implementation of an interior-point filter line-search algorithm for large-scale nonlinear programming. Math. Program., 106(1), 25–57. doi: 10.1007/s10107-004-0559-y
[37] HSL - Home Page. (2023, May 24). Retrieved from https://www.hsl.rl.ac.uk
[16b] Briglia, E., Alaggia, S., & Paganini, F. (2017). Distribution network management based on optimal power flow: Integration of discrete decision variables. 2017 51st Annual Conference on Information Sciences and Systems (CISS). IEEE. doi: 10.1109/CISS.2017.7926079

## Slide 166: References
[20b] Pandey, A., Agarwal, A., & Pileggi, L. (2020). Incremental Model Building Homotopy Approach for Solving Exact AC-Constrained Optimal Power Flow. arXiv, 2011.00587. Retrieved from https://arxiv.org/abs/2011.00587v1
[23b] Pillage, L. (1998). Electronic Circuit & System Simulation Methods (SRE). McGraw-Hill Professional. Retrieved from https://www.amazon.com/Electronic-Circuit-System-Simulation-Methods/dp/0070501696
[24a] Shao, C., Wang, X., Wang, X., Du, C., Dang, C., & Liu, S. (2014). Cooperative Dispatch of Wind Generation and Electric Vehicles With Battery Storage Capacity Constraints in SCUC. IEEE Trans. Smart Grid, 5(5), 2219–2226. doi: 10.1109/TSG.2014.2316911

## Slide 167: References
[inaolaji2021] Inaolaji, A., Savasci, A., Paudyal, S., & Kamalasadan, S. . Accuracy of Phase-Decoupled and Phase-Coupled Distribution Grid Power Flow Models. 2021 IEEE Power & Energy Society Innovative Smart Grid Technologies Conference (ISGT). IEEE. doi: 10.1109/ISGT49243.2021.9372193