## Slide 1: Multi-Period Optimal Power Flow (MP-OPF) for Active Distribution Systems (ADS)
Team WSU
Slides created by
Aryan Ritwajeet Jha, Graduate Research Assistant1
Anup Parajuli, Graduate Research Assistant1
Under the supervision of Dr. Anamika Dubey, Associate Professor1
1 Energy Systems Innovation Center, School of Electrical Engineering and Computer Science, Voiland College of Engineering, Washington State University, Pullman
Notes: Remember to hit the reset button to make sure all the page elements react properly.
There are 20 different layouts that you can choose from.

## Slide 2: Quick Overview of Team WSU’s objectives for the Spokane Connected Communities Project [CC1, CC2]
Developing an optimal control scheme for a distribution feeder with renewables and ‘flexibility-offering’ Edo nodes to optimize a desired objective.
Steps involved:
Validation of optimization algorithm results against known trusted distribution system simulator solutions such as OpenDSS [OD].
Development of mathematical models which can realistically model the components of the system along the lines of known optimization frameworks which can be programmatically solved for.
Development and implementation of decomposition algorithms which can enable the optimization problem to be solved in faster times.

## Slide 3: Quick Overview of the contents of this presentation
Quick overview of the Linear Unbalanced Three-Phase Model and results for the Centralized OPF algorithm
Explanation of the modelling of specific system components in the optimization algorithm followed by the complete Balanced Three-Phase Nonlinear model
Explanation of the procedure required for the Distributed OPF algorithm followed by a comparison of its results vs the Centralized OPF algorithm
Brief overview of WSU’s Test Network Configuration

## Slide 4: WSU’s Test Network
  Test Case: IEEE123 Node System with photovoltaics (PVs) and Batteries
  Network Models:
  Balanced Three-Phase Nonlinear Model with PVs and Batteries for hours.
  Unbalanced Three-Phase Linear (LinDistFlow) Model with PVs and Batteries for hours
Representative Image with DER penetration at of load buses. Penetration Percentages may be varied.

## Slide 5: WSU’s Test Network (contd.)
Penetration of PVs:
  of the Load Buses in terms of number of buses.
  For buses with PVs, in terms of ratio of total demand real power at that bus .
Penetration of Batteries:
of the Load Buses in terms of number of buses. (
For buses with Batteries, rated battery charge/discharge power is of the total demand real power at that bus

## Slide 6: Modelling Edo Nodes as Storage
Grid Edge Devices (GEDs) over multiple participating buildings are aggregated to form Edo Nodes. These can be thought of as reservoirs of energy offering controlled complex power dispatch during a particular time-duration.
Our model is based on the Generalized Battery Model as given in [2].
Modification 1: Zero Idle SOC dissipation
Modification 2: Instead of a , we model non-negative valued such that they’re complementary i.e.
*This is a helpful modification for optimization problems where both variables refer to the net outgoing/incoming power (after a lossy conversion) from the perspective of the distribution grid.
Battery SOC Equation
Initial SOC
Charging/Discharging Limits
SOC Limits

## Slide 7
Reactive Power
Discharging Power
Charging Power
Battery SOC
Inverter Rating
Edo-Node Modelling
as Battery with Inverter
Complementarity Constraint
Relationships between the battery rated powers and inverter rating
Typical kW
Typically,
Typical kVAr
Typically,
Note: Values here are typical in OPF literature [2, 3]

## Slide 8
Edo-Node Modelling
as Battery with Inverter
After full horizon:
Battery SOC Equation
Battery SOC Limits
Initial SOC
Terminal SOC constraint
Reactive Power
Discharging Power
Charging Power
Battery SOC
Inverter Rating
Charging/Discharging Efficiencies
Battery SOC Limits
Note: Values here are typical in OPF literature [2, 3]

## Slide 9
Solar PVs with Inverters
Solar Inverter Rating Limit
Reactive Power
PV Real Power
Inverter Rating
Relationships between the rated powers
Typical kW
Typically,
Typical kVAr
Typically,

## Slide 10
Network Constraints – Branch Flow Model
Bus
Bus
Load
Battery Reactive Power
Discharging Power
Charging Power
PV Reactive Power
PV Real Power
Branch
Branch
Branch
Branch Power Flow
Current Flow
Branch Power Flow
Branch Power Flow
Bus :
Bus :
Engineering Constraints
No backflow allowed
Optionally, Peak Satisfiable Demand may be specified as well

## Slide 11
Network Constraints – Branch Flow Model
Bus
Bus
Load
Battery Reactive Power
Discharging Power
Charging Power
PV Reactive Power
PV Real Power
Branch
Branch
Branch
Branch Power Flow
Current Flow
Branch Power Flow
Branch Power Flow
Bus :
Bus :
Node Real Power Balance
Node Reactive Power Balance
KVL across branch
Current Magnitude across branch
Net Generation at Node

## Slide 12
Full Optimization Model – Balanced Three-Phase Nonlinear OPF
Bus
Bus
Load
Battery Reactive Power
Discharging Power
Charging Power
PV Reactive Power
PV Real Power
Branch
Branch
Branch
Branch Power Flow
Current Flow
Branch Power Flow
Branch Power Flow
Bus :
Bus :
Desired Objective Function, (appended with an SCD penalty function)
Network Constraints
Engineering Constraints
Component Constraints (DERs, Batteries)
Line Losses
Substation Power
Cost of Substation Power
Peak Shaving Constraint
SCD Penalty Function – Ensures that Simultaneous Charging and Discharging for any Battery never occurs
Voltage Deviation

## Slide 13: Network being tested on
ENApp Approach [1]
  Divide the network into several areas to solve for their Optimal Power Flow solutions separately, with exchange of boundary variables after every ‘macro-iteration’.

## Slide 14: Communication Architecture for MP-DOPF Algorithm
OpenDSO-System Operator (Forecast)
OpenDSO-Measurement Devices
OpenDSO-EDO
OpenDSO-OpenDSO
Types of Communication Involved:

## Slide 15
A simple schematic for D-OPF.

## Slide 16: Extension of DOPF to Multi-Period
Start
--------------------------------------------
Known:
---------------------------------------------
while “(Spatial) boundary variables are NOT equal in value for all connected parent-child areas”
    Run OPF for minimizing the losses across the horizon for each area, in parallel. This is called as a macro-iteration.
    Exchange (spatial) boundary variables between all sets of connected parent-child areas.
end
-----------------------------------------------
Stop

## Slide 17
Extending the MP-D-OPF to three time-steps
(: The actual process

## Slide 18
A simpler schematic for MP-D-OPF for three time-steps
(: The decomposed computation paradigm for a single macro-iteration
In one Macro-iteration, each of these ‘green boxes’ is solved for OPF once. Once all boxes are solved, boundary variables are exchanged between each pair of connected areas. This completes a Macro-iteration.

## Slide 19
A simpler schematic for MP-D-OPF for three time-steps
(
Start
--------------------------------------------
Known:
---------------------------------------------
while “(Spatial) boundary variables are still updating in value for all connected parent- child areas across all time-steps”
end
-----------------------------------------------
Stop
Perform 1 MP-DOPF Macro-iteration.
Each green box is one OPF problem.
Note: In one Macro-iteration, each of these green boxes is solved. Once all boxes are solved, boundary variables are exchanged between each pair of connected areas. This completes a Macro-iteration.

## Slide 20: MPCOPF Verified for
strLoadShape = 'New Loadshape.LoadShape npts =10 interval = 1 mult = [0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =10 interval = 1 mult = [0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7]'
MPDOPF Simulation Results
OpenDSS Powerflow Results
OpenDSS Def Profiles
~ hours

## Slide 21: MPCOPF Verified for
strLoadShape = 'New Loadshape.LoadShape npts =10 interval = 1 mult = [0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =10 interval = 1 mult = [0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7]'
OpenDSS Def Profiles
Confirmation of Complementarity of Charging and Discharging (or equivalently, confirmation that no SCD is happening)

## Slide 22: MPDOPF Verified for
strLoadShape = 'New Loadshape.LoadShape npts =10 interval = 1 mult = [0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =10 interval = 1 mult = [0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7]'
MPDOPF Simulation Results
OpenDSS Powerflow Results
OpenDSS Def Profiles
~ minutes

## Slide 23: MPDOPF Verified for
strLoadShape = 'New Loadshape.LoadShape npts =10 interval = 1 mult = [0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =10 interval = 1 mult = [0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7]'
OpenDSS Def Profiles
Confirmation of Complementarity of Charging and Discharging (or equivalently, confirmation that no SCD is happening)

## Slide 24
MPDOPF Verified for
Convergence of Boundary Complex Powers with every macro-iteration
OpenDSS Def Profiles
strLoadShape = 'New Loadshape.LoadShape npts =10 interval = 1 mult = [0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =10 interval = 1 mult = [0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7]'

## Slide 25: Convergence of Boundary Voltages with every macro-iteration
MPDOPF Verified for
OpenDSS Def Profiles
strLoadShape = 'New Loadshape.LoadShape npts =10 interval = 1 mult = [0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =10 interval = 1 mult = [0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7]'

## Slide 26: MPCOPF Verified for
strLoadShape = 'New Loadshape.LoadShape npts =12 interval = 1 mult = [0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =12 interval = 1 mult = [0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4]'
MPDOPF Simulation Results
OpenDSS Powerflow Results
OpenDSS Def Profiles
~ hours

## Slide 27: MPCOPF Verified for
OpenDSS Def Profiles
strLoadShape = 'New Loadshape.LoadShape npts =12 interval = 1 mult = [0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =12 interval = 1 mult = [0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4]'
Confirmation of Complementarity of Charging and Discharging (or equivalently, confirmation that no SCD is happening)

## Slide 28: MPDOPF Verified for
MPDOPF Simulation Results
OpenDSS Powerflow Results
OpenDSS Def Profiles
strLoadShape = 'New Loadshape.LoadShape npts =12 interval = 1 mult = [0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =12 interval = 1 mult = [0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4]'
~ minutes

## Slide 29: MPDOPF Verified for
OpenDSS Def Profiles
strLoadShape = 'New Loadshape.LoadShape npts =12 interval = 1 mult = [0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =12 interval = 1 mult = [0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4]'
Confirmation of Complementarity of Charging and Discharging (or equivalently, confirmation that no SCD is happening)

## Slide 30
MPDOPF Verified for
strLoadShape = 'New Loadshape.LoadShape npts =12 interval = 1 mult = [0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =12 interval = 1 mult = [0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4]'
Convergence of Boundary Complex Powers with every macro-iteration
OpenDSS Def Profiles

## Slide 31: Convergence of Boundary Voltages with every macro-iteration
MPDOPF Verified for
OpenDSS Def Profiles
strLoadShape = 'New Loadshape.LoadShape npts =12 interval = 1 mult = [0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =12 interval = 1 mult = [0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4]'

## Slide 32: MPDOPF Verified for
OpenDSS Def Profiles
strLoadShape = 'New Loadshape.LoadShape npts =16 interval = 1 mult = [0.598 0.613 0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855 0.95 1]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =16 interval = 1 mult = [0 0 0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4 0.1 0]'
MPDOPF Simulation Results
OpenDSS Powerflow Results
~ minutes

## Slide 33: MPDOPF Verified for
OpenDSS Def Profiles
strLoadShape = 'New Loadshape.LoadShape npts =16 interval = 1 mult = [0.598 0.613 0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855 0.95 1]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =16 interval = 1 mult = [0 0 0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4 0.1 0]'
Confirmation of Complementarity of Charging and Discharging (or equivalently, confirmation that no SCD is happening)

## Slide 34
MPDOPF Verified for
strLoadShape = 'New Loadshape.LoadShape npts =16 interval = 1 mult = [0.598 0.613 0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855 0.95 1]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =16 interval = 1 mult = [0 0 0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4 0.1 0]'
Convergence of Boundary Complex Powers with every macro-iteration
OpenDSS Def Profiles

## Slide 35: Convergence of Boundary Voltages with every macro-iteration
MPDOPF Verified for
strLoadShape = 'New Loadshape.LoadShape npts =16 interval = 1 mult = [0.598 0.613 0.644 0.668 0.705 0.75 0.777 0.787 0.796 0.782 0.783 0.789 0.826 0.855 0.95 1]'
strLoadShapePV = 'New Loadshape.LoadShapePV npts =16 interval = 1 mult = [0 0 0.1 0.2 0.3 0.5 0.8 0.9 1 1 0.99 0.9 0.7 0.4 0.1 0]'
OpenDSS Def Profiles

## Slide 36: LinDist OPF: A Linear Modelling for Unbalanced Three-Phase Radial Networks
Assumptions:
Power loss in the branch is much smaller that actual branch power flow (Zjkℓjk << Sjk)
Branch currents not included in power flow formulations (ℓjk=0)
Original OPF LinDist OPF
(Zjkℓjk << Sjk)
Zjkℓjk << Sjk
ℓjk=0
S. H. Low, "Convex Relaxation of Optimal Power Flow—Part I: Formulations and Equivalence," in IEEE Transactions on Control of Network Systems, vol. 1, no. 1, pp. 15-27, March 2014, doi: 10.1109/TCNS.2014.2309732.

## Slide 37: Overall Formulation with PV + Batteries
Real power Flow
Reactive power Flow
KVL
Box constraint on reactive power from DG
Battery S.O.C constraint
Battery charge limit constraint
Discharge power limit
charge power limit
Charge/discharge complementarity constraint
Nodal Voltage Limit
Battery thermal limit
=0

## Slide 38: Battery complementarity constraint:
Modified Objective Function:
f(x) = Loss Minimization/ Cost Minimization
SCD fictitious energy loss, a =1e-3
Phases | a | b | c
Number of lines | 91 | 79 | 88
Pij | 91 | 79 | 88
Qij | 91 | 79 | 88
V | 92 | 80 | 89
Phases | a | b | c
Q(der) | 30 | 30 | 30
Phases | a | b | c
Pd | 30 | 30 | 30
Pc | 30 | 30 | 30
soc | 30 | 30 | 30
Total = 777
Total = 777+90=867
Total no. of der bus= 30
Total no. of battery bus= 30
Total= 777+90+270 = 1137
P(rated) of PV = 30KW.
S(rated) of PV inv = 36KVA
P(rated) of battery = 10KW.
S(rated) of battery inv = 12KVA
E(rated) = P(rated) of battery *4
B = [0.3 E(rated), 0.95 E(rated)]
Pd, Pc = [ 0, P(rated of battery)]
Vmin = 0.95 p.u
Vmax = 1.05 p.u
Initial s.o.c of each batteries = Bmin = 30%
No. of Variables
N. Nazir, P. Racherla and M. Almassalkhi, "Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders," in IEEE Transactions on Power Systems, vol. 35, no. 4, pp. 2683-2692, July 2020

## Slide 39: Loss Minimization
Line Loss saving = 1118 KW

## Slide 40: Cost Minimization
Energy Cost saving = $ 40

## Slide 41: [In development] Simulation Process of Spatially and Temporally Decomposed OPF algorithm.
Start
------------------------------------------------------------------------
Known:
-----------------------------------------------------------------------
while “temporal boundary variables are NOT equal in value for all consecutive time intervals”
  while “spatial boundary variables are NOT equal in value for all connected parent-child areas”
    Run (D-)OPF for minimizing the losses across the horizon for each area, in parallel. This is called as a macro-iteration.
    Exchange spatial boundary variables between all sets of connected parent-child areas.
    end
    Exchange temporal boundary variables between consecutive time intervals
end
------------------------------------------------------------------------
Stop

## Slide 42: Thank You.

## Slide 43: Appendix and References follow

## Slide 44: (IEEE 123 System divided into) 4 Area System

## Slide 45
What is will be done? A ‘true’ MP-DOPF using Differential Dynamic Programming (Currently under formulation, variables not explained here) [3]

## Slide 46: Optimization Formulation
Mixed-Integer Non-linear Optimization Problem (in built-complementarity, but harder to solve)
Line Losses
Real Powerflow from a bus into the network
Reactive Powerflow from a bus into the network
Kirchhoff's Voltage Law (KVL)
Current Magnitude in a branch
Battery State of Charge Equation (this equation is temporally coupled, or has ‘memory’)
Complementarity of Charging and Discharging during a particular time interval.
DER Generation (forecasted, non-controllable)
Loads (forecasted, non-controllable)

## Slide 47: References
[1] Sadnan, R., & Dubey, A. (2021). Distributed Optimization Using Reduced Network Equivalents for Radial Power Distribution Systems. IEEE Trans. Power Syst., 36(4), 3645–3656. doi: 10.1109/TPWRS.2020.3049135
[2] Eilyan Bitar's Papers. (2023, August 16). Coordinated Aggregation
of Distributed Demand-Side Resources. Retrieved from https://bitar.engineering.cornell.edu/papers.html
[3] Pandey, A., Agarwal, A., & Pileggi, L. (2020). Incremental Model Building Homotopy Approach for Solving Exact AC-Constrained Optimal Power Flow. arXiv, 2011.00587. Retrieved from https://arxiv.org/abs/2011.00587v1

## Slide 48: References
[CC1] Spokane Connected Communities Project | GEB. (2024, April 29). Retrieved from https://connectedcommunities.lbl.gov/spokane-connected-communities-project
[CC2 PDF from Department of Energy website
[OD] OpenDSS. (2024, March 25). Retrieved from https://www.epri.com/pages/sa/opendss