## Slide 1: Multi-Period Optimization for Power Distribution Systems with Battery Storage
Aryan Ritwajeet Jha
Notes: Remember to hit the reset button to make sure all the page elements react properly.
There are 20 different layouts that you can choose from.

## Slide 2: Battery Models Used in Various Papers
Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Ensures Complementarity (i.e., ensures absence of SCD) without any additional boolean constraints.
They prefer rectangular coordinates for all complex variables, for usage in Newton Raphson method.
SOC is always taken as energy (base )

## Slide 3: Battery Models Used in Various Papers
Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations

## Slide 4: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Optimization Loops (Time-scales): An ‘Outer’, slower MILP loop for fixing battery SOC values and STL element values.
An ‘Inner’, faster SOCP loop for solving for optimal power flows.
Battery apparent power (through inverter) limits.

## Slide 5: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Optimization Loops (Time-scales): An ‘Outer’, slower MILP loop for fixing battery SOC values and STL element values.
An ‘Inner’, faster SOCP loop for solving for optimal power flows.
Battery apparent power (through inverter) limits.

## Slide 6: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Upon addition of the green block, the grey terms are removed from the constraints.
The yellow block ensures that the terminal battery SOC value (i.e. SOC value at the end of the horizon) prescribed by the outer loop is adhered to.
is also an optimization (control) variable

## Slide 7: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations

## Slide 8: Battery Models Used in Various Papers
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations
For a system WITHOUT any STL elements, instead of a (MI , SOCP) loops, they use (SOCP, NLP) loops.
Battery models themselves are the same.
Also, NO yellow term this time.

## Slide 9: Battery Models Used in Various Papers
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations
For a system WITHOUT any STL elements, instead of a (MI , SOCP) loops, they use (SOCP, NLP) loops.
Battery models themselves are the same.
Also, NO yellow term this time.

## Slide 10: Battery Models Used in Various Papers
Battery Dispatching for End Users With On-Site Renewables and Peak Demand Charges – An Approximate Dynamic Programming Approach
Initial thoughts: It uses a linear/linearized model of the battery, and all equations are expressed with matrices.
Details to be added later.

## Slide 11: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Xiaodong Qian and Yuanguo Zhu
Seventh International Joint Conference on Computational Sciences and Optimization (2014)
Deptt. Of Appl. Math.
Nanjing University of Science and Technology (NUST)
Professor with the Department of Mathematics
NUST, Nanjing, China
Has 1 citation – by the SUGAR-DDP paper by Agarwal and Pileggi

## Slide 12: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Starting with an expression for the Cost-to-go function for an Uncertain Optimal Control Problem.

## Slide 13: Differential Dynamic Programming for Multistage Uncertain Optimal Control
In about equations, it provides an algorithm for solving a stochastic MPC problems using Differential Dynamic Programming (DDP). It initializes the solution using an unspecified Genetic Algorithm (GA).

## Slide 14: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Key equations required for Step 1 of the algorithm:

## Slide 15: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Key equations required for Step 2 of the algorithm:

## Slide 16: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Key equations required for Step 3 of the algorithm:
Given in another reference.

## Slide 17: Differential Dynamic Programming for Multistage Uncertain Optimal Control
At the end it also gives a numerical example utilizing the algorithm.

## Slide 18: Differential Dynamic Programming for Multistage Uncertain Optimal Control
It uses Genetic Algorithms for Initializing the solution.
Given in another reference.

## Slide 19: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Utilizing the key derived equations for the algorithm for this specific problem:

## Slide 20: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Utilizing the key derived equations for the algorithm for this specific problem:

## Slide 21: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Results are on the right.

## Slide 22: Differential Dynamic Programming for Multistage Uncertain Optimal Control
Takeaway:
This paper provides a solid mathematical understanding of the rationale behind Differential Dynamic Programming.
It provides an algorithm along with a conveniently described set of equations which can aid us in solving our own problems using DDP.
Which are generated because we use Taylor’s Linear Approximations.

## Slide 23: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Aayushya Agarwal and Larry Pileggi
IEEE TRANSACTIONS IN POWER SYSTEMS (2022)
PhD student at Carnegie Mellon University (CMU)
Prof. at CMU
Reference papers with: Amritanshu Pandey Assistant Prof. at UVM

## Slide 24: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Objective function is economic-based
Charging/ Discharging cost considered
Charging/Discharging efficiency considered
Ramping of Active Power Generation form Synchronous Generators considered.

## Slide 25: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation
For a single time-period ACOPF, a Lagrange function with dual and slack variables is formed to represent network equality constraints and device limits respectively:

## Slide 26: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation
Where is a vector of dual variables associated with each equality constraint defined in [20b]
In the same reference, is a vector of inequality constraints representing generator active and reactive power limits, bus voltage bounds and line loading constraints with a vector of corresponding slack variables, .
Introduced in SUGAR: is a ‘feasibility current’ at each node and is minimized according to a large weight .
In a feasible optimal dispatch solution, all feasible current sources will be equal to .

## Slide 27: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation
Reference [20b] equations.

## Slide 28: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: Sugar ACOPF
SUGAR defines a set of the modified KKT conditions of representing the first order optimality conditions to ensure a local minimum is reached.
The non-linear KKT equations are solved for using Newton-Raphson.
Each iteration, the Newton-Raphson constructs a Hessian of the .

## Slide 29: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: SUGAR ACOPF – Diode Limiting
Inequality constraints are solved using an interior point method that gradually constrains the function shown in (9).
Each iteration of the interior point method requires robust limiting to ensure variables do not exceed their operating limits.
‘Diode limiting methods’ from [23b] ensure each primal variable and associated slack variable is individually limited, with a factor of and respectively (12-13).
(14-15) represent damping constants to ensure there’s no inter-iteration oscillation of primal/slack variables.

## Slide 30: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: SUGAR ACOPF – Tx-stepping based Homotopy Method
SUGAR accommodates arbitrary initial conditions by employing a homotopy method that relaxes the non-linear constraints to a trivial problem , and then sequentially solves a series of sub-problems to the original problem .
A scalar homotopy factor is embedded into the non-linear ACOPF formulation and is iteratively decreased from to to trace a path in the solution space.
They claim that this works for arbitrary initial conditions and shows robust convergence for ACOPF systems.

## Slide 31: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: Generator Ramping Limits
Generator ramping limits are incorporated in the same way and solved for using an interior-point method.
ESS also incorporated. (Didn’t see or read any explanation on the possibility of SCD, i..e )

## Slide 32: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: MP-OPF
How is Simultaneous Charging Discharging (SCD) avoided?

## Slide 33: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: MP-OPF
Augmented Lagrangian of the MP-OPF problem.

## Slide 34: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Optimization Problem Formulation: MP-OPF
If not for any Generator ramping or ESS constraints, the problem is just a summation of individual ACOPFs.
The authors anyway proceed to solve for each ACOPF individually, but using a Forward-Backward Process.
While solving for time , they assume any variables from as some constants, and solve (‘forward-pass’) to get all variables for time-step .
Then they do a ‘backwards-pass’ to update the sequence based on gradient information from the forward trajectory.
Together, a forward pass and a backward pass produce a new sequence of controls.
If converged, the backward pass does not affect the forward trajectory.

## Slide 35: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Results: 14 Bus System
Gen 02 replaced with an Energy Storage System.
Optimized over 10 hourly time-periods.
Loading factor is the blue curve (min. 1.0, Max. 1.4)
Optimal solution: Charge during periods of low demand (1 to 3), discharge during high loading time (hours 3 to 9). Because discharging cost is much lower than cost of getting power from synchronous machines.
Still, ramping constraints of the synchronous machines restrict the battery from discharging its entire energy.

## Slide 36: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Results: 14 Bus System
Gen 02 replaced with an Energy Storage System.
Optimized over 10 hourly time-periods.
Loading factor is the blue curve (min. 1.0, Max. 1.4)
Optimal solution: Charge during periods of low demand (1 to 3), discharge during high loading time (hours 3 to 9). Because discharging cost is much lower than cost of getting power from synchronous machines.
Still, ramping constraints of the synchronous machines restrict the battery from discharging its entire energy.

## Slide 37: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Results: Synthetic 70k testcase

## Slide 38: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Results: Synthetic 70k testcase
Solving for 10 hours of 70k system data configuration took them 14 minutes on a single-core macbook.

## Slide 39: Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Differential Dynamic Programming: Convergence Analysis
Using Hessians, Gauss-Seidel, spectral radius, positive-definiteness, they prove that for realistic systems, this method always works.

## Slide 40: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Nawaf Nazir and Mads Almassalkhi
Power System Computation Conference (2018)
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Nawaf Nazir, Pavan Racherla and Mads Almassalkhi
IEEE TRANSACTIONS IN POWER SYSTEMS (2020)
Reference [22]

## Slide 41: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Reference [22]
IEEE 123 and 13 bus systems
Unbalanced, Phases assumed to be NOT coupled
Second Order Conic Decomposition (SOCP) used to fix State-of-Charge (SOC) for batteries at every time step. [~1 minute]
Non-Linear Programming (NLP) to solve the individual decoupled time-steps (in parallel). [~ seconds]
Uses the proof on the based on the 2018 paper to assume a relaxation of the complementarity constraint (with suitable augmentation of the objective function).
IEEE 13 bus system
Unbalanced, Phases assumed to be NOT coupled.
STL Elements (Discrete-control)
Optimized slowly using Multi-Integer Linear Programming
Renewables + Battery
Optimized fastly using SOCP
[~1 minute]
Proof given, that for realistic systems, relaxing the hard battery complementarity constraint AND adding a soft constraint to the objective function, makes the problem NOT Mixed-Integer, while still yielding feasibly, near-optimal soltutions.

## Slide 42: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Nawaf Nazir and Mads Almassalkhi
Power System Computation Conference (2018)
Currently at PNNL Then: PhD at University of Vermont (UVM)
Currently Assoc. Prof. at UVM

## Slide 43: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Distribution System
  Unbalanced
  Mechanical Assets?
  Significant Solar Penetration
Two Different Optimization Time-Scales
  A slow time-scale for dispatching discrete mechanical assets using Mixed-Integer Program (MIP)
  A fast time-scale for continuously monitoring DERs using SOCP.

## Slide 44: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Different Optimization Time-Scales
  Different Types of discrete and continuous operated devices.
    E.g. Capacitor/Reactor Banks, Line Regulators (On/Off), Load-Tap-Changing (LTC) Transformers
    Discrete states of these devices render the problem NP-hard. (So, they were NOT NP-hard anyway?)
    McCormick relaxation and linearization techniques have been used to incorporate these devices into the OPF problem for a BALANCED network. [16b]
  This necessitates the use of separate optimization loops to coordinate them.
  Mechanical assets also have operational constraints on tap changes per hour to limit wear and tear, which necessitates separation.

## Slide 45: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Novel hierarchical OPF scheme for separation of the slow-mechanical (discrete control scheme) and fast power-electronic (continuous control scheme) on two different time-scales.
Service Transformer Layers (STL) elements dispatched optimally using Multi-Period three-phase SOCP convex relaxation techniques applied to radial distribution networks for fast corrective control.
Simultaneous charging and discharging of batteries in a convex model of 3-phase system is also analyzed and conditions are provided under which this can be avoided.

## Slide 46: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
AC Three-phase Non-Linear Model (Plant)
Minutely Dispatch of Flexible Assets (SOCP)
Hourly Dispatch of Mechanical Assets (MILP)
Forecast and Analytics
Flowchart showing the Hierarchical time-scale control algorithm

## Slide 47: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Want to minimize number of changes in mechanical discrete control components to reduce wear and tear.
  Aim: minimize from a nominal set-point using operation of these discrete assets.
  The outer loop also schedules active power exchanges of the STL elements, considering the variability of solar PV generation and forecast energy demands.
  Reactive Power Control of STL elements reserved for corrective control, in the Inner Loop.
Outer Loop Formulation: Voltage Positioning

## Slide 48: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Since discrete decision variables only take integer values, the outer loop problem becomes a mixed-integer problem, which is NP-hard.
  Branch and bound techniques can be effective on MIPs if their continuous versions are convex.
  In order to reduce the computational complexity of the outer loop, a three-phase LINEARIZED model of the network is used.
  This reduces the problem to a Mixed-Integer Linear Program (MILP).
Outer Loop Formulation : Voltage Positioning

## Slide 49: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  STL Architecture
    Four-Quadrant Control Scheme. Can supply and consume both and .
    Each STL element is composed of a renewable source of energy such as solar power and some form of storage like a battery bank.
Outer Loop Formulation : Voltage Positioning
Solar PV
Battery
Inverter
Inverter
Transmission Network.

## Slide 50: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Aim: minimize in the network.
    while keeping track of a power reference signal from the transmission level.
    while keeping the system within operational bounds.
  This program optimizes the STL elements over the fast time-scale.
  This corrective optimization loop is required to be fast ( minute).
  Three-phase SOCP used to solve the optimization problem.
    A Branch Flow Model (BFM) is used to represent the power flow equations.
Inner Loop Formulation: Corrective OPF

## Slide 51: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  The Inner Loop optimization problem can thus be formulated as:
  <INSERT formulae (26) to (36)>
    Inner Loop Objective function
    Power Balance Equation (BFM)
    Power Flow Equations (BFM)
    Line Power Flow Constraints
      Relation between BFM sub-matrices
    Voltage Constraint
    Solar PV Constraint
    Node Power Relations
    Battery State of Charge and Complementarity Constraints
Inner Loop Formulation: Corrective OPF

## Slide 52: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Complementarity: Charging and Discharging are complementary phenomenon for a battery, i.e. at NO time step, can a battery simultaneously undergo charging and discharging.
  Complementarity Constraints ensure that Batteries never charge and discharge simultaneously.
    But these constraints make the SOCP of the Inner Loop Non-Convex.
    One way to make it convex would be to use Mixed-Integer SOCP in the Outer Loop.
      But that would make increase the computation time substantially.
      We h0wever want solution time (to obtain a near-optimal solution) to be minute.
      So not doing that.
Relaxing Complementarity Constraint

## Slide 53: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Complementarity Constraints ensure that Batteries never charge and discharge simultaneously.
    But these constraints make the SOCP of the Inner Loop Non-Convex.
    One way to make it convex would be to use Mixed-Integer SOCP in the Outer Loop.
      But that would make increase the computation time substantially.
      We h0wever want solution time (to obtain a near-optimal solution) to be minute.
      Instead our approach is to relax these constraints and analyze the conditions where the optimal solution still respects them.
Relaxing Complementarity Constraint

## Slide 54: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
      Instead, their approach is to relax these constraints and analyze the conditions where the optimal solution still respects them.
      In [23b], [24b], authors provide conditions under which complementarity is satisfied in the optimal solution for an economic dispatch problem.
        In [24b], KKT conditions are analyzed for a DC model of an economic dispatch problem and they show that under realistic assumptions, complementarity is respected.
        In this paper, the analysis is extended to a distribution system setting where the objective is to minimize line losses, while considering four quadrant battery operation.
Relaxing Complementarity Constraint

## Slide 55: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
Inner Loop Formulation: Corrective OPF

## Slide 56: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
Inner Loop Formulation: Corrective OPF

## Slide 57: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
    Additional ‘loss functions’ for 1. Penalizing SCD and 2. Respecting Battery SOC Limits.
Inner Loop Formulation: Corrective OPF

## Slide 58: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
IEEE 13
Unbalanced
has 1-phase, 2-phase, 3-phase lines
A Three-phase OLTC transformer between 633 and 634
Capacitor Banks placed at 675 and 611
STL elements added at nodes 632, 675, 680, 684
  These STL elements each have:
    Solar PV generation
    Battery capable of four-quadrant operation.
Test Cases and Numerical Simulations
Modified IEEE 13 bus system used.

## Slide 59: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Nawaf Nazir, Pavan Racherla and Mads Almassalkhi
IEEE TRANSACTIONS IN POWER SYSTEMS (2020)
Currently at PNNL PhD at University of Vermont (UVM)
Currently Asst. Prof. at UVM
Currently Assoc. Prof. at UVM

## Slide 60: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Distribution System
  Unbalanced
  Inverter-Interfaced
  Significant Solar Penetration
Three-Phase Unbalanced
  Non-Convex Loss-minimization problem
  Formulated as a Convex Second Order Conic Program (SOCP) for arriving at an initial solution for Non-Linear Program (NLP)
  NLP run to ensure physically realizable solution

## Slide 61: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Conditions derived to ensure that batteries do NOT simultaneously charge and discharge. (Is that a big problem?)
Tested with GridLab-D for IEEE 13 and IEEE 123.
  AC feasibility of the solutions ensured
  Near-optimal performance
  Solution time < 1 min.

## Slide 62: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
ConEd* of NY moving towards Distributed System Platforms (DSPs)
These DSPs allow for DERs to be factored into Optimization schemes for Power Generation
DERs can be Optimized to function as Virtual Batteries (VBs)
  provide energy services at different spatio-temporal scales.
* Consolidated Edison, electric utility in NY and NOT ComEd, Commonwealth Edison, electric utility in IL

## Slide 63: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Traditionally, DistFlow algorithms based on the Branch Flow Model (BFM), which are an exact non-linear formulation of the distribution power flow equations, only work on balanced single-phase equivalent networks.
  But Distribution Networks are inherently unbalanced.

## Slide 64: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  In [22] by the same authors, they have developed a three-phase convex SOCP relaxation of the multi-period OPF problem, and provided sufficient conditions which ensure the avoidance of simultaneous charging and discharging.
  In this paper, they extend the work by developing a Multi-Period SOCP-NLP algorithm that provides a near optimal and guaranteed feasible solution.

## Slide 65: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  The optimized solutions from the relaxed SOCP model, are used to initialize a Non-Linear Program (NLP) of the actual AC Power Flow, to obtain a physically realizable solution.
  Real-Power Solutions that form the energy trajectory and are obtained from the SOCP, are fixed in the NLP, leading to a decoupling of the different time-steps. (What? How?)
  As a result, the NLP solves for each time-step separately (possibly in-parallel), leading to a scalable framework. (What?)
  Validation is performed using GridLab-D.

## Slide 66: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  IEEE , Unbalanced,
  Algorithm implemented in Receding-Horizon fashion.
  Receding-Horizon means a rolling window where predictions for the next time-steps from time to are made at time and since predictions are updated at every time step, for the next time step , predictions for the next time steps from to are once again made.
  The cycle goes on.
Fig. Aggregate solar, demand and net-demand profile over a prediction horizon of

## Slide 67: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
The SOCP solution outputs an optimal battery and inverter control schedule
The schedule is used by the NLP to calculate a physically realizable schedule
The physically realizable schedule is implemented by GridLab-D to determine the resulting AC Power Flows.
The forecast of demand and renewable generations are updated.
The Process

## Slide 68: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
The Process
Fig. Coupling of SOCP with NLP by fixing real power solutions from SOCP and hence decoupling the NLP to obtain a feasible solution. (What? How?)
Fig. Available reactive power variation range for NLP across multiple time-steps based on the active power trajectory provided by the SOCP.

## Slide 69: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  Distributed Storage and Solar PV Units randomly added to nodes
    They can supply active and reactive power through four quadrant operation.
    Each storage unit has capacity and apparent power rating
    Each solar PV unit has a rating
  Solar and Load Profile prediction horizon
    Each step

## Slide 70: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  Three-phase OPF is run in a receding horizon fashion with prediction horizon of time-steps, for the dispatch of controllable assets of the network to minimize network losses.
  Set-points provided by the solutions of the SOCP are used to initialize an NLP to provide a feasible solution.
    SOCP modeled in JuMP, with Julia and solved using GUROBI.
      Multi-period SOCP has
        kvariables (k as in thousand)
        k linear constraints
        k SOC constraints

## Slide 71: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
    NLP also modeled in JuMP, but solved using IPOPT [36] using the HSL_MA86 solver [37]
      A single-period of the Multi-period SOCP has
        kvariables
        k linear constraints
        k SOC constraints
        k non-linear constraints

## Slide 72: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
    levels for both loads (low and high) and solar PV generation (low and high)
    ‘High’ implies Base Values for both Loads as well as solar PV
    ‘Low’ implies of the base values in both cases.
    Thus scenarios are modeled:
      LL (Low Solar, Low Loads)
      LH (Low Solar, High Loads)
      HL (High Solar, Low Loads)
      HH (High Solar, High Loads)
Different Solar and Load Cases

## Slide 73: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Run 1: SOCP with NO Complementarity constraint added to objective function.
  Run 2: SOCP with Complementarity constraint added to objective function.
  Run 3: MI Problem which inherently solves with the Complementarity condition.

## Slide 74: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Run 1: Gives a Physically unrealizable solution.
  Run 2 and Run 3: Give the SAME feasible solution.

## Slide 75: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Run 2 and Run 3: Give the SAME feasible solution.
  Also, the SAME Optimal solution.

## Slide 76: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Optimality gap always below 3% for different solar penetration levels.
  Feasible solutions always ( difference).
  Solution times
  NLP total time assuming parallelized operation over every single time step.
Table: Comparison of the Optimality Gap Values of SOCP and NLP.

## Slide 77: References
[22] Nazir, N., & Almassalkhi, M. (2018). Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices. 2018 Power Systems Computation Conference (PSCC). IEEE. doi: 10.23919/PSCC.2018.8442555
[36] Wächter, A., & Biegler, L. T. (2006). On the implementation of an interior-point filter line-search algorithm for large-scale nonlinear programming. Math. Program., 106(1), 25–57. doi: 10.1007/s10107-004-0559-y
[37] HSL - Home Page. (2023, May 24). Retrieved from https://www.hsl.rl.ac.uk
[16b] Briglia, E., Alaggia, S., & Paganini, F. (2017). Distribution network management based on optimal power flow: Integration of discrete decision variables. 2017 51st Annual Conference on Information Sciences and Systems (CISS). IEEE. doi: 10.1109/CISS.2017.7926079

## Slide 78: References
[20b] Pandey, A., Agarwal, A., & Pileggi, L. (2020). Incremental Model Building Homotopy Approach for Solving Exact AC-Constrained Optimal Power Flow. arXiv, 2011.00587. Retrieved from https://arxiv.org/abs/2011.00587v1
[23b] Pillage, L. (1998). Electronic Circuit & System Simulation Methods (SRE). McGraw-Hill Professional. Retrieved from https://www.amazon.com/Electronic-Circuit-System-Simulation-Methods/dp/0070501696
[24a] Shao, C., Wang, X., Wang, X., Du, C., Dang, C., & Liu, S. (2014). Cooperative Dispatch of Wind Generation and Electric Vehicles With Battery Storage Capacity Constraints in SCUC. IEEE Trans. Smart Grid, 5(5), 2219–2226. doi: 10.1109/TSG.2014.2316911