## Slide 1: Multi-Period Optimization for Power Distribution Systems with Battery Storage
Aryan Ritwajeet Jha
Notes: Remember to hit the reset button to make sure all the page elements react properly.
There are 20 different layouts that you can choose from.

## Slide 2: Multi-Period D-OPF simulation of a grid with DERs and Battery Storage
Currently it’s a series of single period D-OPFs, being solved for greedily.
Battery State of Charge (SOC) is ‘memorized’ by the grid after every time step, so a meaningful simulation is run for ‘Multi-time period’, even though the optimization itself is NOT done over the whole horizon.
Naïve Brute-Force approach to MPOPF being implemented (Solve for the full problem for the full horizon in one go).

## Slide 3: The Network
Current problem statement:
  Single-phase power distribution network (Here, the IEEE123 Node Test System)

## Slide 4: The Network
Current problem statement:
  Divide the network into several areas in order to solve for their Optimal Power Flow solutions separately, with exchange of boundary variables after every ‘macro-iteration’.

## Slide 5: (IEEE 123 System divided into) 4 Area System

## Slide 6: Optimization Formulation
The Full Optimization Problem for Brute-Force MPOPF
#Types of variables
#Variables
#Equality Constraints
(Non-Linear)

## Slide 7: Optimization Formulation
The Full Optimization Problem for Brute-Force MPOPF
#Types of variables
#Variables
#Equality Constraints
(Non-Linear)

## Slide 8: Problem Statement
  Given the State of Charges (SOC or ) of all batteries in a grid at any time , along with other non-controllable parameter values like :
  Solve for Optimal Power Flow of the system, with the objective of minimizing line losses
  while making sure that:
  1. (the SOC of the battery at the end of the simulation) stays in permissible limits
  2. For no node containing a battery, is . In other words, make sure that Complementarity of Discharging and Charging is ensured. Alternatively, Simultaneous Charging and Discharging (SCD) is avoided.

## Slide 9: Simulation Parameters
Objective: Minimize Line Losses (Greedily)
System: IEEE Node System
Phase: Balanced
Supply: DERs and Batteries at select (about of total) nodes. Substation.
Demand: Flat line (will be made varying each time-step in future simulations)
Control: Inverter Reactive Power Control for DERs and Batteries. Battery Charging/Discharging.
Number of discrete time-steps:
Duration per time-step: min.

## Slide 10: Simulation Process
Start
mark within the permissible range.
while
  Batteries start with state at the beginning of the time interval.
  Run (D-)OPF for minimizing the losses during current time interval to
  Batteries reach a state after the end of the interval, as per the optimal solution.
  Repeat with .
end

## Slide 11: Optimization Formulation
The Full Optimization Problem: Linear Objective, Non-Linear Constraint
Fixed values accounted for into .
#Types of variables
#Variables
#Equality Constraints (Non-Linear)
Most Complicated Scenario Possible
Will happen when every node has a DER and a Battery
SCD Term (Green Box)

## Slide 12: Bounds and Values
Battery State/Control Variables

## Slide 13: Bounds and Values
– The Coefficient for the Green Box term penalizing SCD

## Slide 14: A metric for quantifying effect of storage and DER power on the grid.
More savings in losses and substation power through batteries.
Power flowing into the area indirectly via the substation (directly for Area 1).
Solar generated power for the whole area.
Net real power injected into the area via batteries.

## Slide 15: Results: Real Power Losses
vs
While batteries have charge to spare, the losses are minimized, as less power needs to flow all the way from the substation.
Here, for the first time-periods, or , the batteries are able to discharge at their maximum capacity, and so the line losses are significantly lower. By time-periods, they completely run out of SOC (reach minimum value of SOC), and the losses return to ‘normal’, pre-battery configuration.

## Slide 16: Results: Reactive Power Losses
vs
Investigate further. I thought that since batteries don’t generate Real Power when they run out of SOC, they should generate more reactive power. I guess more real power flow is highly coupled with more reactive power flow? Need to check values.

## Slide 17: Results
vs
Machine dependent AND still varies every run.
My personal machine
My Lab machine
To do: Clarify the values in the plot and the ones in the logs. How exactly are they different again?

## Slide 18: Results
vs

## Slide 19: Results: Boundary Variables
vs
Investigate: Negative Reactive Power Flowing from Area 1 to Area 3 and Area 2 to Area 4? Check reactive generation values for the areas.
As expected.

## Slide 20: Results: Battery Variables
, vs
This plot is for one battery, specified by an Area and Node (for that area).
The plots for other batteries are near identical, as only SOC percentages have been plotted instead of absolute battery charge in
Batteries initially discharge at maximum rate, which helps in:
Loss Minimization
Voltage Deviation Minimization (not explicitly solved for, but noted from the plots of node voltages)
until they reach their minimum permissible SOC.
Zero charging. (will plot together later to clearly highlight that)

## Slide 21: Results
Simulation went in an intuitive manner.
Batteries ONLY discharged. They kept discharging until their State of Charge dipped to the minimum permissible value of , i.e.
. This is intuitive, as for a greedy minimization of line-losses with no perspective of any future opportunity costs for not being able to discharge, the batteries have no incentive to charge, and all the incentive to discharge.
Other variables depend on the above fact. For the first time-periods ( of simulation-time), while the batteries haven’t run out of charge, line losses , Substation Power are kept significantly lower, and savings due to batteries is high for every area. By the time-periods, soar to ‘battery-less’ levels, an drops to a low, constant value.
Multi-Period D-OPF of IEEE Node System

## Slide 22: Takeaways
Handle SCD (Green Box) term with care.
While it has helped us relax the constraint of Boolean Variables in the optimization modelling and solving, it needs extra caution for modelling in order to arrive at a useful solution.
For example, it cannot be used alone without the main objective function, such as loss minimization. Otherwise, the optimizer will penalize any participation of the batteries, making both and for all batteries.
needs to be carefully designed. The value of the SCD Green Box should be within a magnitude range of the line loss function’s value. Too greater, and it would reduce battery power to zero, too low, and SCD might occur.
The cost of replacing the Boolean Constraints with the SCD Green Box term for avoiding SCD.

## Slide 23: Takeaways
However, if we use an economic based model, which assigns a cost to substation power and battery charging/discharging, then the number of optimization steps can be reduced to just two, with one initialization with no line losses, as is a state variable itself which does not require any other non-linear equality constraint term like .
But in that case, we need to clarify who owns the storage (cite that paper), as the coefficient for cost function of battery charging/discharging could then be either positive or negative (how?).
The cost of replacing the Boolean Constraints with the SCD Green Box term for avoiding SCD.

## Slide 24: Reference of Notation

## Slide 25: Reference of Notation
Helpful for clarifying any variable in the optimization formulations.

## Slide 26: Battery Models Used in Various Papers
Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
Ensures Complementarity (i.e., ensures absence of SCD) without any additional boolean constraints.
They prefer rectangular coordinates for all complex variables, for usage in Newton Raphson method.
SOC is always taken as energy (base )

## Slide 27: Battery Models Used in Various Papers
Large Scale Multi-Period Optimal Power Flow With Energy Storage Systems Using Differential Dynamic Programming
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations

## Slide 28: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Optimization Loops (Time-scales): An ‘Outer’, slower MILP loop for fixing battery SOC values and STL element values.
An ‘Inner’, faster SOCP loop for solving for optimal power flows.
Battery apparent power (through inverter) limits.

## Slide 29: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Optimization Loops (Time-scales): An ‘Outer’, slower MILP loop for fixing battery SOC values and STL element values.
An ‘Inner’, faster SOCP loop for solving for optimal power flows.
Battery apparent power (through inverter) limits.

## Slide 30: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Upon addition of the green block, the grey terms are removed from the constraints.
The yellow block ensures that the terminal battery SOC value (i.e. SOC value at the end of the horizon) prescribed by the outer loop is adhered to.
is also an optimization (control) variable

## Slide 31: Battery Models Used in Various Papers
Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations

## Slide 32: Battery Models Used in Various Papers
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations
For a system WITHOUT any STL elements, instead of a (MI , SOCP) loops, they use (SOCP, NLP) loops.
Battery models themselves are the same.
Also, NO yellow term this time.

## Slide 33: Battery Models Used in Various Papers
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
All variables are Continuous
No Discrete variables
No Boolean variables
In the final equations
For a system WITHOUT any STL elements, instead of a (MI , SOCP) loops, they use (SOCP, NLP) loops.
Battery models themselves are the same.
Also, NO yellow term this time.

## Slide 34: Battery Models Used in Various Papers
Battery Dispatching for End Users With On-Site Renewables and Peak Demand Charges – An Approximate Dynamic Programming Approach
Initial thoughts: It uses a linear/linearized model of the battery, and all equations are expressed with matrices.
Details to be added later.