## Slide 1: MPOPF Simulation and OpenDSS Validation
Aryan Ritwajeet Jha
Graduate Research Assistant
Washington State University
Notes: Remember to hit the reset button to make sure all the page elements react properly.
There are 20 different layouts that you can choose from.

## Slide 2: How do other authors validate their OPF results?
[nazir2020tpwrs]
Feasibility of Solution: Forward-Backward Sweep in GridLab-D.
They check violation of node voltages between the simulation and the GridLab-D powerflow.
Optimality of Solution:
The authors argue that a) computing (even for verifying) Multi-Period NL OPF can be computationally too expensive and b) the solution to a ‘Decoupled’ NL-OPF (with battery set points already assigned by the Full Horizon SOCP OPF will provide an even lower optimal value compared to the Full Horizon NLP OPF (7).

## Slide 3: How do other authors validate their OPF results?
[nazir2020tpwrs]
Optimality of Solution:
They formulate their optimality gap as a comparison between the SOCP optimal value and Decoupled NLP optimal value (9), for each time-step, and taking the maximum optimality gap to show as the result.
For IEEE 123, they get a maximum optimality gap of . Violations against GridLab-D are small. (Feasible solution).

## Slide 4: How do other authors validate their OPF results?
[nazir2020tpwrs]
Commentary on Solution Times:
Fig. (a) They see a similar trend in results as me when performing a Full Horizon NLP, with solution times becoming increasingly larger as the time-horizon increases.
Fig. (b) But their SOCP approach scales well, with solutions times increasingly almost linearly with time-horizon. For practical scenarios (day-ahead hourly simulation), their SOCP solution converges in under a minute.

## Slide 5: How do other authors validate their OPF results?
[usman2022tpwrs]
Feasibility and Optimality of Solution:
They mainly showcase the benchmarks based on UK bus system.
They solve the full horizon (day-ahead hourly) OPF MINLP OPF in JuMP using BONMIN solver (here called ).
They compare its objective function against their own linearized method (here called ).
They get an optimality gap of less than .
Infeasibilities are detected based on box-constraints (line-limits breached, bus voltage limits breached, etc.).

## Slide 6: How do other authors validate their OPF results?
[agrawal2022tpwrs]
Other authors, sometimes use a different solution paradigm, and compare it against MATLAB’s fmincon.

## Slide 7: Latest Slides End Here.
Previous Slides Follow

## Slide 8: MPCOPF Simulation has been verified for X% PVs and Y% Batteries Only for small horizons () because of long simulation time.

## Slide 17: sim terminated at 100 micro-iterations

## Slide 18: sim terminated at 100 micro-iterations

## Slide 28: MPCOPF Simulation has been verified for X% PVs and Y% Batteries Only for small horizons () because of long simulation time.
MPCOPF Simulation Results
These slides will show results for a -hour (hourly) PV Battery Simulation Validation for IEEE system, but I’ve validated for many other percentage penetrations too, for smaller time-steps.
For example, even this simulation took seconds on my GB Office PC.
Even for the same , increasing the GED penetration % increases the OPF solution time.
And even for small GED penetration percentage (10% each like the one done in these slides), increasing increases the simulation time by a lot.

## Slide 29: MPCOPF Simulation has been verified for X% PVs and Y% Batteries Only for small horizons () because of long simulation time.
MPCOPF Simulation Results
OpenDSS Powerflow Results
PVs + Batteries

## Slide 30: Current Issue: Some mismatch in MPCOPF results Seeming mismatch between specified (from OPF) and assigned values (into OpenDSS) for Battery Reactive Powers

## Slide 31: Currently Doing: Extracting Results on an Hourly (Time-step) Basis, for hourly comparison against OpenDSS

## Slide 32: IEEE PVs, Batteries. COPF.
Multi-Period Simulation, T = 1, Batteries at 0%, DERs at 0% ( buses)
OpenDSS Powerflow with DERs at 0% ( buses)
Objective Function values (Real Power Losses ) and System-wide Voltage snapshots (shown in the next slides) match.
This slide:

## Slide 33: IEEE PVs, Batteries. COPF.
Multi-Period Simulation, T = 1, Batteries at 0%, DERs at 50% ( buses)
OpenDSS Powerflow with DERs at 50% ( buses)
Objective Function values (Real Power Losses ) and System-wide Voltage snapshots (shown in the next slides) match.
This slide:

## Slide 34: IEEE PVs, Batteries. COPF.
Multi-Period Simulation, T = 1, Batteries at 0%, DERs at 100% ( buses)
OpenDSS Powerflow with DERs at 100% ( buses)
Objective Function values (Real Power Losses ) and System-wide Voltage snapshots (shown in the next slides) match.
This slide:

## Slide 35: Comparison with OpenDSS: System-wide Voltage Snapshots PV = Battery =

## Slide 36
Comparison with OpenDSS: System-wide Voltage Snapshots PV = Battery =

## Slide 37: Comparison with OpenDSS: System-wide Voltage Snapshots Battery = PV =

## Slide 38
Comparison with OpenDSS: System-wide Voltage Snapshots
PV = Battery =

## Slide 39
Comparison with OpenDSS: System-wide Voltage Snapshots
PV and Battery =

## Slide 40: Trying to benchmark the “Benchmark” Simulation against the “Original” Simulation
“Benchmark” Simulation: MP-(C/D)-OPF
: Number of Time-Periods (tunable)
: Number of Areas the system is divided into. The simulation becomes:
CMPOPF if
DMPOPF if
DERs (tunable): ( to buses)
Batteries# (tunable*): ( to buses)
“Original” Simulation: (C/D)-OPF
No Time-dimension: Equivalent to
: Number of Areas the system is divided into. The simulation becomes:
CMPOPF if
DMPOPF if
DERs (fixed): ( buses)
No Batteries: Equivalent to ( buses)

## Slide 41: Trying to benchmark the “Benchmark” Simulation against the “Original” Simulation
“Benchmark” Simulation: MP-(C/D)-OPF
: Number of Time-Periods (tunable)
: Number of Areas the system is divided into. The simulation becomes:
CMPOPF if
DMPOPF if
DERs (tunable): ( to buses)
Batteries#(tunable*): ( to buses)
“Original” Simulation: (C/D)-OPF
No Time-dimension: Like
: Number of Areas the system is divided into. The simulation becomes:
CMPOPF if
DMPOPF if
DERs (fixed): ( buses)
No Batteries: Like ( buses)
#Batteries add more than just new decision variables (which are ) to the simulation.
Incorporating them (while avoiding mixed-integer programming) requires specifying additional ‘soft-constraint’ objective functions to the optimizer, including an “SCD penalty” function and a “Deviation of terminal SOC from a reference SOC penalty” function, which require additional unknown parameters (such as in my simulation). Ideally, these ‘soft-constraint’ function values in the result should be zero, but if this doesn’t happen, they cannot be truly compared to a ‘battery-free’ simulation.
*Note: The way the batteries are currently modeled, they can only be placed at a bus where there is already a DER. (So only buses are eligible to have a battery)

## Slide 42: Trying to benchmark the “Benchmark” Simulation against the “Original” Simulation
But, if batteries are removed (unmodeled) from the MPOPF simulation, the previously mentioned complications are also avoided, and thus the two simulations can be compared toe-to-toe. This is what I’ve been doing recently.
“Benchmark” Simulation: MP-(C/D)-OPF
: Number of Time-Periods (tunable)
: Number of Areas the system is divided into. The simulation becomes:
CMPOPF if
DMPOPF if
DERs (tunable): ( to buses)
Batteries# (tunable*): ( to buses)
“Original” Simulation: (C/D)-OPF
No Time-dimension: Equivalent to
: Number of Areas the system is divided into. The simulation becomes:
CMPOPF if
DMPOPF if
DERs (fixed): ( buses)
No Batteries: Equivalent to ( buses)
(COPF)

## Slide 43: IEEE DER, Batteries. COPF.
Multi-Period Simulation, T = 1, Batteries at 0%, DERs at 100% ( buses)
OpenDSS Powerflow with DERs at 100% ( buses)
Current Status: My MPCOPF line loss result matches with the previous COPF line loss results, which still is a little off the OpenDSS line loss. Voltages (on the next page) match closely, but not completely. I don’t know the cause of the slight mismatch. (and whether it will blow up for bigger simulations, or not be an issue)

## Slide 44: Comparison with OpenDSS

## Slide 45: IEEE DER, Batteries. COPF.
Multi-Period Simulation, T = 1, Batteries at 0%, DERs at 100% ( buses)
Original Simulation* DERs at 100% ( buses)
* Original Simulation = Simulation used by Rabayet to model DOPF on IEEE Bus System with DERs ( buses). Obviously, there’s no element of time not modeled, so and no batteries (not modeled, so )
Problem: These values should be the same. This is an OPF modelling issue.

## Slide 46: Current Approach: Validating OPF decision variables with OpenDSS
By setting
Running Powerflow in OpenDSS, obtaining and comparing against my simulation (checking for physical violations, but also, just checking the two vs bus-number curves in general).
I’m writing an OpenDSS validator function, which takes busData, branchData, for a given time-interval and plots its powerflow voltages against my .

## Slide 47: Comparison with OpenDSS confirms that the current MPCOPF model has issues

## Slide 48: References
[nazir2018pscc] Nazir, N., & Almassalkhi, M. . Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices. 2018 Power Systems Computation Conference (PSCC). IEEE. doi: 10.23919/PSCC.2018.8442555
[nazir2020tpwrs] Nazir, N., Racherla, P., & Almassalkhi, M. (2020). Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders. IEEE Trans. Power Syst., 35(4), 2683–2692. doi: 10.1109/TPWRS.2019.2963249
[usman2022tpwrs] Usman, M., & Capitanescu, F. (2022). A Novel Tractable Methodology to Stochastic Multi-Period AC OPF in Active Distribution Systems Using Sequential Linearization Algorithm. IEEE Trans. Power Syst., 38(4), 3869–3883. doi: 10.1109/TPWRS.2022.3197884